## October 24
|  |  | FSTPP I&II |  | FSTPP III |  | KhSTPP I |  | KhSTPP II |  | TSTPS-I |  | BARH-1 |  | BARH-2 |  | BRBCL |  | DARLIPALLI |  | NORTH KARANPURA |  | NPGC |  | GMR |  | MPL |  | Adhunik |  | JITPL |  | Tashiding |  | Teesta III |  | Teesta V
S.No. | Particulars | Dimension | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs | FRC for GENERTAION loss event of around 1114 MW in DB power generating station , Western Region control areas on 21st October 2024 at 16:49 hrs
|  |  | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data
1 | Actual Net Interchange before the Event, PA (Import +ve / Export -ve) | MW | -1492.8368 | -1587 | -475.9373 | -503 | -684.5466 | DATA NOT RECEIVED | -1349.6299 | -1433.26 | -845.3461 | -922 | -1104.0143 | -1188 | -1232.486 | -1301 | -652.2681 | -729.6334 | -1507.9663 | -1585 | -633.1032 | -666 | -1911.7244 | -1977.69 | -632.9455 | -679 | -1005.2203 | -1040 | -487.5331 | -526.45 | -1132.8003 | -1191 | -67.7442 | DATA NOT RECEIVED | PLANT OUT | PLANT OUT | PLANT OUT | PLANT OUT
2 | Actual Net Interchange after the Event, PB (Import +ve / Export -ve) | MW | -1500.5232 | -1617 | -477.3817 | -504 | -693.7972 |  | -1349.5792 | -1431.37 | -849.8492 | -923 | -1117.2927 | -1210 | -1238.088 | -1306 | -654.4847 | -734.3178 | -1513.4374 | -1592 | -633.1032 | -668 | -1915.0546 | -1986.25 | -637.1253 | -687 | -1001.7321 | -1037 | -487.7073 | -526.253 | -1133.6005 | -1190 | -67.7442
3 | Change in net interchange, PB-PA (2 - 1) | MW | -7.6864 | -29.7 | -1.4444 | -0.4 | -9.2507 |  | 0.050659 | 1.9 | -4.5032 | -0.9 | -13.2784 | -22 | -5.6021 | -5 | -2.2166 | -4.7 | -5.4711 | -6.6 | 0 | -1.9 | -3.3302 | -8.6 | -4.1798 | -7.8 | 3.4883 | 2.9 | -0.17426 | 0.2 | -0.80017 | 0.1 | 0
4 | Generation Loss (+) / Load Throw off (-) during the Event, PL | MW | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Control Area Response, ΔP=(PB-PA) – PL (3-4) | MW | -7.6864 | -29.7 | -1.4444 | -0.4 | -9.2507 |  | 0.050659 | 1.9 | -4.5032 | -0.9 | -13.2784 | -22 | -5.6021 | -5 | -2.2166 | -4.7 | -5.4711 | -6.6 | 0 | -1.9 | -3.3302 | -8.6 | -4.1798 | -7.8 | 3.4883 | 2.9 | -0.17426 | 0.2 | -0.80017 | 0.1 | 0
6 | Frequency before the Event, fA | HZ | 49.998 | 49.998 | 49.998 | 49.998 | 49.998 |  | 49.998 | 49.998 | 49.998 | 49.998 | 49.998 | 49.998 | 49.998 | 49.998 | 49.998 | 49.998 | 49.998 | 49.998 | 49.998 | 49.998 | 49.998 | 49.998 | 49.998 | 49.998 | 49.998 | 49.998 | 49.998 | 49.998 | 49.998 | 49.998 | 49.998
7 | Frequency after the Event, fB | HZ | 49.965 | 49.965 | 49.965 | 49.965 | 49.965 |  | 49.965 | 49.965 | 49.965 | 49.965 | 49.965 | 49.965 | 49.965 | 49.965 | 49.965 | 49.965 | 49.965 | 49.965 | 49.965 | 49.965 | 49.965 | 49.965 | 49.965 | 49.965 | 49.965 | 49.965 | 49.965 | 49.965 | 49.965 | 49.965 | 49.965
8 | Change in Frequency, Δf=(fB-fA) (7-6) | HZ | -0.033 | -0.03 | -0.033 | -0.033 | -0.033 |  | -0.033 | -0.03 | -0.033 | -0.03 | -0.033 | -0.03 | -0.033 | -0.03 | -0.033 | -0.03 | -0.033 | -0.03 | -0.033 | -0.03 | -0.033 | -0.03 | -0.033 | -0.03 | -0.033 | -0.03 | -0.033 | -0.03 | -0.033 | -0.03 | -0.033
9 | Frequency Response Characteristic, ΔP/ Δf (5 / 8) | MW/Hz | 232.9213 | 901 | 43.7696 | 12 | 280.3234 |  | -1.5351 | -57 | 136.4598 | 27 | 402.377 | 667 | 169.7591 | 153 | 67.1701 | 142 | 165.79 | 201 | 0 | 58 | 100.9152 | 259 | 126.6609 | 236 | -105.7055 | -89 | 5.2805 | -6 | 24.2476 | -3 | 0
10 | Frequency Response Obligation (FRO) of each control area | MW/Hz | 70.5703 | 71 | 26.2492 | 26 | 35.4067 |  | 72.6405 | 73 | 54.3898 | 54 | 42.8225 | 43 | 58.1913 | 58 | 46.3904 | 46 | 83.2963 | 83 | 37.8559 | 38 | 105.6464 | 106 | 37.5454 | 38 | 53.179 | 53 | 24.3789 | 24 | 59.5735 | 60 | 4.1895
11 | Frequency Response Performance (FRP) (9/10) |  | 3.3006 | 12.76 | 1.6675 | 0.46 | 7.9172 |  | -0.021133 | -0.79 | 2.5089 | 0.5 | 9.3964 | 15.57 | 2.9173 | 2.63 | 1.4479 | 3.0599 | 1.9904 | 2.42 | 0 | 1.539 | 0.95522 | 2.46 | 3.3735 | 6.3 | -1.9877 | -1.68 | 0.2166 | -0.25 | 0.40702 | -0.05778 | 0
Consideration of FRP for computation of Average Monthly FRP, Beta ‘ß’ |  |  | 1 | 1 | 1 | 0.46 | 1 | 0 | 0 | 0 | 1 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0.95 | 1 | 1 | 1 | 0 | 0 | 0.21 | 0 | 0.4 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| REMARKS BY RLDC | [19 empty] | SCADA DATA FREEZE
| Beta For OCT 2024 |  |  | 1 |  | 0.46 |  | 1 |  | 0 |  | 0.5 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 0 |  | 0 |  | 0 |  | 0 |  | NA |  | NA
Considerations for Beta Calculation
IN CASE OF NON RECEIPT OF DATA, ERLDC SCADA DATA HAS BEEN USED TO CALCULATED AVERAGE BETA
IN CASE OF PLANT OUTAGE DURING ANY EVENT, THAT EVENT WILL BE EXCLUDED FROM BETA CALCULATION
IN CASE OF PLANT DATA FREEZE DURING ANY EVENT, ERLDC SCADA WLL BE USED FOR BETA CALCULATION
THE FRP VALUE & BETA WILL BE TRUNCATED TO 2 DECIMAL POINTS
If FRP for an event is less than or equal to 0, FRP (Event i) shall be equal to 0.
If FRP for an event lies between 0 to 1, FRP (Event i) shall be equal to the calculated value.
If FRP for an event is greater than or equal to 1, FRP (Event i) shall be equal to 1.

## September 24
|  |  | FSTPP I&II |  | FSTPP III |  | KhSTPP I |  | KhSTPP II |  | TSTPS-I |  | BARH-1 |  | BARH-2 |  | GMR |  | MPL |  | Adhunik |  | JITPL |  | BRBCL |  | Tashiding |  | NPGC |  | DARLIPALLI |  | NORTH KARANPURA |  | Teesta III |  | Teesta V
S.No. | Particulars | Dimension | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs
|  |  | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data
1 | Actual Net Interchange before the Event, PA (Import +ve / Export -ve) | MW | -871.9915 | -896 | -258.2812 | -289 | -408.6157 | DATA NOT RECEIVED | -499.5464 | -542.7 | -260.3412 | -290 | -345.7851 | -377 | -685.7583 | -725 | -304.2764 | data not received | -568.2213 | -590 | -190.7778 | -210 | -1079.9008 | -1080 | -487.2612 | -550 | -106.732 | DATA NOT RECEIVED | -1036.0481 | -1086.62 | -819.9547 | -885 | -638.614 | -686 | 0 | PLANT OUT | 0 | PLANT OUT
2 | Actual Net Interchange after the Event, PB (Import +ve / Export -ve) | MW | -870.908 | -895 | -259.7266 | -289 | -410.9554 |  | -501.77 | -543.93 | -260.3412 | -292 | -347.9631 | -379 | -684.7628 | -718 | -304.5513 |  | -565.6898 | -591 | -191.6566 | -211 | -1078.2004 | -1078 | -485.2708 | -552 | -106.8011 |  | -1039.3558 | -1091.91 | -825.355 | -875 | -646.7086 | -693 | 0 |  | 0
3 | Change in net interchange, PB-PA (2 - 1) | MW | 1.0834 | 0.9 | -1.4453 | 0.4 | -2.3397 |  | -2.2236 | -1.2 | 0 | -1.9 | -2.178 | -2.2 | 0.99554 | 6.9 | -0.2749 |  | 2.5315 | -1.5 | -0.87878 | -0.8 | 1.7003 | 1.7 | 1.9905 | -1.6 | -0.069107 |  | -3.3077 | -5.3 | -5.4003 | 10.8 | -8.0946 | -7 | 0 |  | 0
4 | Generation Loss (+) / Load Throw off (-) during the Event, PL | MW | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
5 | Control Area Response, ΔP=(PB-PA) – PL (3-4) | MW | 1.0834 | 0.9 | -1.4453 | 0.4 | -2.3397 |  | -2.2236 | -1.2 | 0 | -1.9 | -2.178 | -2.2 | 0.99554 | 6.9 | -0.2749 |  | 2.5315 | -1.5 | -0.87878 | -0.8 | 1.7003 | 1.7 | 1.9905 | -1.6 | -0.069107 |  | -3.3077 | -5.3 | -5.4003 | 10.8 | -8.0946 | -7 | 0 |  | 0
6 | Frequency before the Event, fA | HZ | 50.229 | 50.229 | 50.229 | 50.229 | 50.229 |  | 50.229 | 50.229 | 50.229 | 50.229 | 50.229 | 50.229 | 50.229 | 50.229 | 50.229 |  | 50.229 | 50.229 | 50.229 | 50.229 | 50.229 | 50.229 | 50.229 | 50.229 | 50.229 |  | 50.229 | 50.229 | 50.229 | 50.229 | 50.229 | 50.229 | 50.024 |  | 50.024
7 | Frequency after the Event, fB | HZ | 50.144 | 50.144 | 50.144 | 50.144 | 50.144 |  | 50.144 | 50.144 | 50.144 | 50.144 | 50.144 | 50.144 | 50.144 | 50.144 | 50.144 |  | 50.144 | 50.144 | 50.144 | 50.144 | 50.144 | 50.144 | 50.144 | 50.144 | 50.144 |  | 50.144 | 50.144 | 50.144 | 50.144 | 50.144 | 50.144 | 49.983 |  | 49.983
8 | Change in Frequency, Δf=(fB-fA) (7-6) | HZ | -0.085 | -0.09 | -0.085 | -0.085 | -0.085 |  | -0.085 | -0.09 | -0.085 | -0.09 | -0.085 | -0.09 | -0.085 | -0.09 | -0.085 |  | -0.085 | -0.09 | -0.085 | -0.09 | -0.085 | -0.09 | -0.085 | -0.09 | -0.085 |  | -0.085 | -0.09 | -0.085 | -0.09 | -0.085 | -0.09 | -0.041 |  | -0.041
9 | Frequency Response Characteristic, ΔP/ Δf (5 / 8) | MW/Hz | -12.7463 | -10 | 17.0037 | -4 | 27.5261 |  | 26.1604 | 14 | 0 | 22 | 25.624 | 26 | -11.7123 | -82 | 3.2341 |  | -29.7823 | 17 | 10.3386 | 10 | -20.0037 | -20 | -23.4174 | 19 | 0.81302 |  | 38.9146 | 62 | 63.5333 | -127 | 95.2306 | 83 | 0 |  | 0
10 | Frequency Response Obligation (FRO) of each control area | MW/Hz | 70.5703 | 71 | 26.2492 | 26 | 35.4067 |  | 72.6405 | 73 | 54.3898 | 54 | 42.8225 | 43 | 58.1913 | 58 | 37.5454 |  | 53.179 | 53 | 24.3789 | 24 | 59.5735 | 60 | 46.3904 | 46 | 4.1895 |  | 105.6464 | 106 | 83.2963 | 83 | 37.8559 | 38 | 51.3606 |  | 27.8375
11 | Frequency Response Performance (FRP) (9/10) |  | -0.18062 | -0.1471 | 0.64778 | -0.16 | 0.77743 |  | 0.36014 | 0.2 | 0 | 0.41 | 0.59838 | 0.6 | -0.20127 | -1.4 | 0.08614 |  | -0.56004 | 0.33 | 0.42408 | 0.4 | -0.33578 | -0.34 | -0.50479 | 0.41 | 0.19406 |  | 0.36835 | 0.59 | 0.76274 | -1.52 | 2.5156 | 2.182 | NA |  | NA
Consideration of FRP for computation of Average Monthly FRP, Beta ‘ß’ |  |  | 0 | 0 | 0.64 | 0 | 0.77 | 0 | 0.36 | 0.2 | 0 | 0.41 | 0.59 | 0.6 | 0 | 0 | 0.08 | 0 | 0 | 0.33 | 0.42 | 0.4 | 0 | 0 | 0 | 0.41 | 0.19 | 0 | 0.36 | 0.59 | 0.76 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Beta For all |  |  | 0 |  | 0 |  | 0.77 |  | 0.2 |  | 0.41 |  | 0.6 |  | 0 |  | 0.08 |  | 0.33 |  | 0.4 |  | 0 |  | 0.41 |  | 0.19 |  | 0.59 |  | 0 |  | 1 |  | NA |  | NA
Considerations for Beta Calculation
IN CASE OF NON RECEIPT OF DATA, ERLDC SCADA DATA HAS BEEN USED TO CALCULATED AVERAGE BETA
IN CASE OF PLANT OUTAGE DURING ANY EVENT, THAT EVENT WILL BE EXCLUDED FROM BETA CALCULATION
IN CASE OF PLANT DATA FREEZE DURING ANY EVENT, ERLDC SCADA WLL BE USED FOR BETA CALCULATION
THE FRP VALUE & BETA WILL BE TRUNCATED TO 2 DECIMAL POINTS
If FRP for an event is less than or equal to 0, FRP (Event i) shall be equal to 0.
If FRP for an event lies between 0 to 1, FRP (Event i) shall be equal to the calculated value.
If FRP for an event is greater than or equal to 1, FRP (Event i) shall be equal to 1.

## August 24
|  |  | FSTPP I&II |  | FSTPP III |  | KhSTPP I |  | KhSTPP II |  | TSTPS-I |  | BARH-1 |  | BARH-2 |  | GMR |  | MPL |  | Adhunik |  | JITPL |  | BRBCL |  | Tashiding |  | NPGC |  | DARLIPALLI |  | NORTH KARANPURA |  | Teesta III |  | Teesta V
S.No. | Particulars | Dimension | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs | FRC for thE RE GENERTAION loss event of around 1200 MW in Tamilnadu , Southern Region control areas on 23rd August 2024 at 12:34 hrs
|  |  | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data
1 | Actual Net Interchange before the Event, PA (Import +ve / Export -ve) | MW | -885.7018 | -908.8775 | -296.1733 | -317.503 | -420.3813 | DATA NOT RECEIVED | -506.4574 | -547.5647 | -263.0478 | -294.5 | -409.3145 | -444.9 | -696.4589 | -728.1034 | -534.1254 | -577.9046 | -564.5686 | -587.14 | -240.1013 | -259.7311 | -1130.1012 | -1130.1012 | -502.4316 | -553.9269 | -106.59 | DATA NOT RECEIVED | -1041.9661 | -1095.6645 | -736.0839 | -792.5252 | -714.0013 | -767.9462 | 0 |  | 0
2 | Actual Net Interchange after the Event, PB (Import +ve / Export -ve) | MW | -893.3281 | -907.1863 | -306.6808 | -325.4895 | -419.6761 |  | -509.4252 | -548.9089 | -263.6812 | -291.1 | -421.2361 | -453.3 | -704.4066 | -732.8645 | -540.8889 | -579.6646 | -564.6113 | -587.67 | -244.2717 | -265.3582 | -1128.3994 | -1128.3994 | -523.8681 | -565.0218 | -107.01 |  | -1039.2123 | -1085.3522 | -746.0588 | -800.606 | -741.0351 | -782.1512 | 0 |  | 0
3 | Change in net interchange, PB-PA (2 - 1) | MW | -7.6263 | 1.6912 | -10.5074 | -7.9865 | 0.70523 |  | -2.9678 | -1.3442 | -0.63336 | 3.4 | -11.9215 | -8.4 | -7.9477 | -4.7611 | -6.7635 | -1.76 | -0.042664 | -0.53 | -4.1703 | -5.6271 | 1.7018 | 1.7018 | -21.4365 | -11.0949 | -0.4 |  | 2.7538 | 10.3123 | -9.9749 | -8.0808 | -27.0338 | -14.205 | 0 |  | 0
4 | Generation Loss (+) / Load Throw off (-) during the Event, PL | MW | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
5 | Control Area Response, ΔP=(PB-PA) – PL (3-4) | MW | -7.6263 | 1.6912 | -10.5074 | -7.9865 | 0.70523 |  | -2.9678 | -1.3442 | -0.63336 | 3.4 | -11.9215 | -8.4 | -7.9477 | -4.7611 | -6.7635 | -1.76 | -0.042664 | -0.53 | -4.1703 | -5.6271 | 1.7018 | 1.7018 | -21.4365 | -11.0949 | -0.4 |  | 2.7538 | 10.3123 | -9.9749 | -8.0808 | -27.0338 | -14.205 | 0 |  | 0
6 | Frequency before the Event, fA | HZ | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 |  | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 |  | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.024 |  | 50.024
7 | Frequency after the Event, fB | HZ | 49.957 | 49.957 | 49.957 | 49.957 | 49.957 |  | 49.957 | 49.957 | 49.957 | 49.957 | 49.957 | 49.957 | 49.957 | 49.957 | 49.957 | 49.957 | 49.957 | 49.957 | 49.957 | 49.957 | 49.957 | 49.957 | 49.957 | 49.957 | 49.957 |  | 49.957 | 49.957 | 49.957 | 49.957 | 49.957 | 49.957 | 49.983 |  | 49.983
8 | Change in Frequency, Δf=(fB-fA) (7-6) | HZ | -0.049 | -0.049 | -0.049 | -0.049 | -0.049 |  | -0.049 | -0.049 | -0.049 | -0.049 | -0.049 | -0.049 | -0.049 | -0.049 | -0.049 | -0.049 | -0.049 | -0.049 | -0.049 | -0.049 | -0.049 | -0.049 | -0.049 | -0.049 | -0.05 |  | -0.049 | -0.049 | -0.049 | -0.049 | -0.049 | -0.049 | -0.041 |  | -0.041
9 | Frequency Response Characteristic, ΔP/ Δf (5 / 8) | MW/Hz | 155.6384 | -34.5153 | 214.4371 | 162.9898 | -14.3925 |  | 60.5681 | 27.4327 | 12.9258 | -69.3878 | 243.2961 | 171.4286 | 162.1978 | 97.1655 | 138.0304 | 35.9184 | 0.87069 | 10.8163 | 85.1082 | 114.8388 | -34.7302 | -34.7302 | 437.4794 | 226.4265 | 8 |  | -56.1997 | -210.4551 | 203.5697 | 164.9145 | 551.7092 | 289.898 | 0 |  | 0
10 | Frequency Response Obligation (FRO) of each control area | MW/Hz | 70.5703 | 70.5703 | 26.2492 | 26.2492 | 35.4067 |  | 72.6405 | 72.6405 | 54.3898 | 54.3898 | 42.8225 | 42.8225 | 58.1913 | 58.1913 | 37.5454 | 37.5454 | 53.179 | 53.179 | 24.3789 | 24.3789 | 59.5735 | 59.5735 | 46.3904 | 46.3904 | 4 |  | 105.6464 | 105.6464 | 83.2963 | 83.2963 | 37.8559 | 37.8559 | 51.3606 |  | 27.8375
11 | Frequency Response Performance (FRP) (9/10) |  | 2.2054 | -0.48909 | 8.1693 | 6.2093 | -0.40649 |  | 0.83381 | 0.37765 | 0.23765 | -1.2758 | 5.6815 | 4.0032 | 2.7873 | 1.6698 | 3.6764 | 0.95667 | 0.016373 | 0.20339 | 3.4911 | 4.7106 | -0.58298 | -0.58298 | 9.4304 | 4.8809 | 2.02 |  | -0.53196 | -1.9921 | 2.4439 | 1.9799 | 14.5739 | 7.6579 | NA |  | NA
Consideration of FRP for computation of Average Monthly FRP, Beta ‘ß’ |  |  | 1 | 0 | 1 | 1 | 0 | 0 | 0.83 | 0.37 | 0.23 | 0 | 1 | 1 | 1 | 1 | 1 | 0.95 | 0.01 | 0.2 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | NA | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Beta For all |  |  | 0 |  | 1 |  | 0 |  | 0.37 |  | 0 |  | 1 |  | 1 |  | 0.95 |  | 0.2 |  | 1 |  | 0 |  | 1 |  | 1 |  | 0 |  | 1 |  | 1 |  | NA |  | NA
Considerations for Beta Calculation
IN CASE OF NON RECEIPT OF DATA, ERLDC SCADA DATA HAS BEEN USED TO CALCULATED AVERAGE BETA
IN CASE OF PLANT OUTAGE DURING ANY EVENT, THAT EVENT WILL BE EXCLUDED FROM BETA CALCULATION
IN CASE OF PLANT DATA FREEZE DURING ANY EVENT, ERLDC SCADA WLL BE USED FOR BETA CALCULATION
THE FRP VALUE & BETA WILL BE TRUNCATED TO 2 DECIMAL POINTS
If FRP for an event is less than or equal to 0, FRP (Event i) shall be equal to 0.
If FRP for an event lies between 0 to 1, FRP (Event i) shall be equal to the calculated value.
If FRP for an event is greater than or equal to 1, FRP (Event i) shall be equal to 1.

## July 24
|  |  | FSTPP I&II |  | FSTPP III |  | KhSTPP I |  | KhSTPP II |  | TSTPS-I |  | BARH-1 |  | BARH-2 |  | GMR |  | MPL |  | Adhunik |  | JITPL |  | BRBCL |  | Tashiding |  | NPGC |  | DARLIPALLI |  | NORTH KARANPURA |  | Teesta III |  | Teesta V
S.No. | Particulars | Dimension | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs | FRC for the load loss event of around 1580 MW in Haryana and Delhi control areas on 16th July 2024 at 22:10 hrs
|  |  | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data
1 | Actual Net Interchange before the Event, PA (Import +ve / Export -ve) | MW | -1032.5525 | -1113.1347 | Plant out | Plant out | -509.9478 | DATA NOT RECEIVED | -1154.3805 | -1235.737 | -888.371 | -959.3 | -558.499 | -629 | -1222.0779 | -1268.5938 | -325.5605 | -351.2289 | -1013.1196 | -1048.5479 | -484.9613 | -484.9613 | -564.5002 | -564.5002 | -679.6567 | DATA NOT RECEIVED | -106.3864 | DATA NOT RECEIVED | -1910.4187 | -1954.0116 | -1507.2294 | -1585.175 | -1254.468 | -1312.0756 | 0 |  | 0
2 | Actual Net Interchange after the Event, PB (Import +ve / Export -ve) | MW | -1022.6907 | -1105.3472 |  |  | -509.0439 |  | -1154.3805 | -1233.4543 | -883.1403 | -940.8 | -559.3552 | -629.3 | -1210.5068 | -1255.8405 | -319.7449 | -345.948 | -1011.7137 | -1046.9654 | -483.9859 | -483.9859 | -564.2998 | -564.2998 | -676.4837 |  | -106.3864 |  | -1910.4187 | -1964.7129 | -1511.9885 | -1574.578 | -1227.0507 | -1287.9245 | 0 |  | 0
3 | Change in net interchange, PB-PA (2 - 1) | MW | 9.8618 | 7.7876 |  |  | 0.90384 |  | 0 | 2.2827 | 5.2307 | 18.5 | -0.8562 | -0.3 | 11.571 | 12.7534 | 5.8156 | 5.2809 | 1.4059 | 1.5825 | 0.97546 | 0.97546 | 0.20044 | 0.20044 | 3.173 |  | 0 |  | 0 | -10.7013 | -4.7592 | 10.597 | 27.4174 | 24.1511 | 0 |  | 0
4 | Generation Loss (+) / Load Throw off (-) during the Event, PL | MW | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
5 | Control Area Response, ΔP=(PB-PA) – PL (3-4) | MW | 9.8618 | 7.7876 |  |  | 0.90384 |  | 0 | 2.2827 | 5.2307 | 18.5 | -0.8562 | -0.3 | 11.571 | 12.7534 | 5.8156 | 5.2809 | 1.4059 | 1.5825 | 0.97546 | 0.97546 | 0.20044 | 0.20044 | 3.173 |  | 0 |  | 0 | -10.7013 | -4.7592 | 10.597 | 27.4174 | 24.1511 | 0 |  | 0
6 | Frequency before the Event, fA | HZ | 50.006 | 50.006 |  |  | 50.006 |  | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 |  | 50.006 |  | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.006 | 50.024 |  | 50.024
7 | Frequency after the Event, fB | HZ | 50.092 | 50.092 |  |  | 50.092 |  | 50.092 | 50.092 | 50.092 | 50.092 | 50.092 | 50.092 | 50.092 | 50.092 | 50.092 | 50.092 | 50.092 | 50.092 | 50.092 | 50.092 | 50.092 | 50.092 | 50.092 |  | 50.092 |  | 50.092 | 50.092 | 50.092 | 50.092 | 50.092 | 50.092 | 49.983 |  | 49.983
8 | Change in Frequency, Δf=(fB-fA) (7-6) | HZ | 0.086 | 0.086 |  |  | 0.086 |  | 0.086 | 0.086 | 0.086 | 0.086 | 0.086 | 0.086 | 0.086 | 0.086 | 0.086 | 0.086 | 0.086 | 0.086 | 0.086 | 0.086 | 0.086 | 0.086 | 0.086 |  | 0.086 |  | 0.086 | 0.086 | 0.086 | 0.086 | 0.086 | 0.086 | -0.041 |  | -0.041
9 | Frequency Response Characteristic, ΔP/ Δf (5 / 8) | MW/Hz | 114.6723 | 90.5533 |  |  | 10.5098 |  | 0 | 26.543 | 60.8215 | 215.1163 | -9.9558 | -3.4884 | 134.547 | 148.2948 | 67.6227 | 61.4058 | 16.3475 | 18.4011 | 11.3426 | 11.3426 | 2.3307 | 2.3307 | 36.8958 |  | 0 |  | 0 | -124.4337 | -55.339 | 123.2209 | 318.8065 | 280.8267 | 0 |  | 0
10 | Frequency Response Obligation (FRO) of each control area | MW/Hz | 45.3666 | 45.3666 |  |  | 22.7614 |  | 46.6975 | 46.6975 | 34.9649 | 34.9649 | 27.5288 | 27.5288 | 37.4087 | 37.4087 | 24.1363 | 24.1363 | 34.1865 | 34.1865 | 15.6721 | 15.6721 | 38.2973 | 38.2973 | 29.8224 |  | 2.6932 |  | 67.9155 | 67.9155 | 53.5476 | 53.5476 | 24.3359 | 24.3359 | 51.3606 |  | 27.8375
11 | Frequency Response Performance (FRP) (9/10) |  | 2.5277 | 1.996 |  |  | 0.46174 |  | 0 | 0.5684 | 1.7395 | 6.1524 | -0.36165 | -0.12672 | 3.5967 | 3.9642 | 2.8017 | 2.5441 | 0.47819 | 0.53826 | 0.72374 | 0.72374 | 0.060858 | 0.060858 | 1.2372 |  | 0 |  | 0 | -1.8322 | -1.0335 | 2.3011 | 13.1002 | 11.5396 | NA |  | NA
Consideration of FRP for computation of Average Monthly FRP, Beta ‘ß’ |  |  | 1 | 1 | plant out | plant out | 0.46 | 0 | 0 | 0.56 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 0.47 | 0.53 | 0.72 | 0.72 | 0.06 | 0.06 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | -1 | [13 empty] | -1
| Remarks(Given by RLDC) | [7 empty] | SCADA DATA FREEZE | [17 empty] | SCADA DATA FREEZE |  | SCADA DATA FREEZE | [5 empty] | PLANT OUT |  | PLANT OUT
| Beta For all |  |  | 1 |  | N/A |  | 0.46 |  | 0.56 |  | 1 |  | 0 |  | 1 |  | 1 |  | 0.53 |  | 0.72 |  | 0.06 |  | 1 |  | 0 |  | 0 |  | 1 |  | 1
Considerations for Beta Calculation
IN CASE OF NON RECEIPT OF DATA, ERLDC SCADA DATA HAS BEEN USED TO CALCULATED AVERAGE BETA
IN CASE OF PLANT OUTAGE DURING ANY EVENT, THAT EVENT WILL BE EXCLUDED FROM BETA CALCULATION
IN CASE OF PLANT DATA FREEZE DURING ANY EVENT, ERLDC SCADA WLL BE USED FOR BETA CALCULATION
THE FRP VALUE & BETA WILL BE TRUNCATED TO 2 DECIMAL POINTS
If FRP for an event is less than or equal to 0, FRP (Event i) shall be equal to 0.
If FRP for an event lies between 0 to 1, FRP (Event i) shall be equal to the calculated value.
If FRP for an event is greater than or equal to 1, FRP (Event i) shall be equal to 1.

## June 24
|  |  | FSTPP I&II | [9 empty] | FSTPP III | [9 empty] | KhSTPP I | [9 empty] | KhSTPP II | [9 empty] | TSTPS-I | [10 empty] | BARH-1 | [9 empty] | BARH-2 | [9 empty] | GMR | [9 empty] | MPL | [9 empty] | Adhunik | [9 empty] | JITPL | [10 empty] | BRBCL | [9 empty] | Tashiding | [9 empty] | NPGC | [9 empty] | DARLIPALLI | [9 empty] | NORTH KARANPURA | [12 empty] | Teesta III | [7 empty] | Teesta V | [7 empty] | TALA | [7 empty] | CHUKHA | [7 empty] | Chujachen
S.No. | Particulars | Dimension | Event-1 : 1090 MW RE generation in Rajasthan at 10:26 hrs_04.06.2024_solar |  | Event-2: 1295 MW RE Gen Loss in Rajasthan at 10:34:36 hrs_04.06.2024_solar |  | Event-3: 1601 MW load loss at Delhi at 14:10 hrs_11.06.2024 |  | Event-4: NR demand experienced a reduction in load of the order of 16.5 GWat 13:53:00 hrs_17.06.2024 |  | Event-5: 4480 MW Gen Loss in NR at 12:42 hrs_19.06.2024 |  | Event-1 : 1090 MW RE generation in Rajasthan at 10:26 hrs_04.06.2024 |  | Event-2: 1295 MW RE Gen Loss in Rajasthan at 10:34:36 hrs_04.06.2024 |  | Event-3: 1601 MW load loss at Delhi at 14:10 hrs_11.06.2024 |  | Event-4: NR demand experienced a reduction in load of the order of 16.5 GWat 13:53:00 hrs_17.06.2024 |  | Event-5: 4480 MW Gen Loss in NR at 12:42 hrs_19.06.2024 |  | Event-1 : 1090 MW RE generation in Rajasthan at 10:26 hrs_04.06.2024 |  | Event-2: 1295 MW RE Gen Loss in Rajasthan at 10:34:36 hrs_04.06.2024 |  | Event-3: 1601 MW load loss at Delhi at 14:10 hrs_11.06.2024 |  | Event-4: NR demand experienced a reduction in load of the order of 16.5 GWat 13:53:00 hrs_17.06.2024 |  | Event-5: 4480 MW Gen Loss in NR at 12:42 hrs_19.06.2024 |  | Event-1 : 1090 MW RE generation in Rajasthan at 10:26 hrs_04.06.2024 |  | Event-2: 1295 MW RE Gen Loss in Rajasthan at 10:34:36 hrs_04.06.2024 |  | Event-3: 1601 MW load loss at Delhi at 14:10 hrs_11.06.2024 |  | Event-4: NR demand experienced a reduction in load of the order of 16.5 GWat 13:53:00 hrs_17.06.2024 |  | Event-5: 4480 MW Gen Loss in NR at 12:42 hrs_19.06.2024 |  | Event-1 : 1090 MW RE generation in Rajasthan at 10:26 hrs_04.06.2024 |  | Event-2: 1295 MW RE Gen Loss in Rajasthan at 10:34:36 hrs_04.06.2024 |  |  | Event-3: 1601 MW load loss at Delhi at 14:10 hrs_11.06.2024 |  | Event-4: NR demand experienced a reduction in load of the order of 16.5 GWat 13:53:00 hrs_17.06.2024 |  | Event-5: 4480 MW Gen Loss in NR at 12:42 hrs_19.06.2024 |  | Event-1 : 1090 MW RE generation in Rajasthan at 10:26 hrs_04.06.2024 |  | Event-2: 1295 MW RE Gen Loss in Rajasthan at 10:34:36 hrs_04.06.2024 |  | Event-3: 1601 MW load loss at Delhi at 14:10 hrs_11.06.2024 |  | Event-4: NR demand experienced a reduction in load of the order of 16.5 GWat 13:53:00 hrs_17.06.2024 |  | Event-5: 4480 MW Gen Loss in NR at 12:42 hrs_19.06.2024 |  | Event-1 : 1090 MW RE generation in Rajasthan at 10:26 hrs_04.06.2024 |  | Event-2: 1295 MW RE Gen Loss in Rajasthan at 10:34:36 hrs_04.06.2024 |  | Event-3: 1601 MW load loss at Delhi at 14:10 hrs_11.06.2024 |  | Event-4: NR demand experienced a reduction in load of the order of 16.5 GWat 13:53:00 hrs_17.06.2024 |  | Event-5: 4480 MW Gen Loss in NR at 12:42 hrs_19.06.2024 |  | Event-1 : 1090 MW RE generation in Rajasthan at 10:26 hrs_04.06.2024 |  | Event-2: 1295 MW RE Gen Loss in Rajasthan at 10:34:36 hrs_04.06.2024 |  | Event-3: 1601 MW load loss at Delhi at 14:10 hrs_11.06.2024 |  | Event-4: NR demand experienced a reduction in load of the order of 16.5 GWat 13:53:00 hrs_17.06.2024 |  | Event-5: 4480 MW Gen Loss in NR at 12:42 hrs_19.06.2024 |  | Event-1 : 1090 MW RE generation in Rajasthan at 10:26 hrs_04.06.2024 |  | Event-2: 1295 MW RE Gen Loss in Rajasthan at 10:34:36 hrs_04.06.2024 |  | Event-3: 1601 MW load loss at Delhi at 14:10 hrs_11.06.2024 |  | Event-4: NR demand experienced a reduction in load of the order of 16.5 GWat 13:53:00 hrs_17.06.2024 |  | Event-5: 4480 MW Gen Loss in NR at 12:42 hrs_19.06.2024 |  | Event-1 : 1090 MW RE generation in Rajasthan at 10:26 hrs_04.06.2024 |  | Event-2: 1295 MW RE Gen Loss in Rajasthan at 10:34:36 hrs_04.06.2024 |  | Event-3: 1601 MW load loss at Delhi at 14:10 hrs_11.06.2024 |  | Event-4: NR demand experienced a reduction in load of the order of 16.5 GWat 13:53:00 hrs_17.06.2024 |  | Event-5: 4480 MW Gen Loss in NR at 12:42 hrs_19.06.2024 |  | Event-1 : 1090 MW RE generation in Rajasthan at 10:26 hrs_04.06.2024 |  |  | Event-2: 1295 MW RE Gen Loss in Rajasthan at 10:34:36 hrs_04.06.2024 |  | Event-3: 1601 MW load loss at Delhi at 14:10 hrs_11.06.2024 |  | Event-4: NR demand experienced a reduction in load of the order of 16.5 GWat 13:53:00 hrs_17.06.2024 |  | Event-5: 4480 MW Gen Loss in NR at 12:42 hrs_19.06.2024 |  | Event-1 : 1090 MW RE generation in Rajasthan at 10:26 hrs_04.06.2024 |  | Event-2: 1295 MW RE Gen Loss in Rajasthan at 10:34:36 hrs_04.06.2024 |  | Event-3: 1601 MW load loss at Delhi at 14:10 hrs_11.06.2024 |  | Event-4: NR demand experienced a reduction in load of the order of 16.5 GWat 13:53:00 hrs_17.06.2024 |  | Event-5: 4480 MW Gen Loss in NR at 12:42 hrs_19.06.2024 |  | Event-1 : 1090 MW RE generation in Rajasthan at 10:26 hrs_04.06.2024 |  | Event-2: 1295 MW RE Gen Loss in Rajasthan at 10:34:36 hrs_04.06.2024 |  | Event-3: 1601 MW load loss at Delhi at 14:10 hrs_11.06.2024 |  | Event-4: NR demand experienced a reduction in load of the order of 16.5 GWat 13:53:00 hrs_17.06.2024 |  | Event-5: 4480 MW Gen Loss in NR at 12:42 hrs_19.06.2024 |  | Event-1 : 1090 MW RE generation in Rajasthan at 10:26 hrs_04.06.2024 |  | Event-2: 1295 MW RE Gen Loss in Rajasthan at 10:34:36 hrs_04.06.2024 |  | Event-3: 1601 MW load loss at Delhi at 14:10 hrs_11.06.2024 |  | Event-4: NR demand experienced a reduction in load of the order of 16.5 GWat 13:53:00 hrs_17.06.2024 |  | Event-5: 4480 MW Gen Loss in NR at 12:42 hrs_19.06.2024 |  | Event-1 : 1090 MW RE generation in Rajasthan at 10:26 hrs_04.06.2024 |  | Event-2: 1295 MW RE Gen Loss in Rajasthan at 10:34:36 hrs_04.06.2024 |  | Event-3: 1601 MW load loss at Delhi at 14:10 hrs_11.06.2024 |  | Event-4: NR demand experienced a reduction in load of the order of 16.5 GWat 13:53:00 hrs_17.06.2024 |  | Event-5: 4480 MW Gen Loss in NR at 12:42 hrs_19.06.2024 |  | Event-1 : 1090 MW RE generation in Rajasthan at 10:26 hrs_04.06.2024 |  |  | Event-2: 1295 MW RE Gen Loss in Rajasthan at 10:34:36 hrs_04.06.2024 |  |  | Event-3: 1601 MW load loss at Delhi at 14:10 hrs_11.06.2024 |  |  | Event-4: NR demand experienced a reduction in load of the order of 16.5 GWat 13:53:00 hrs_17.06.2024 |  | Event-5: 4480 MW Gen Loss in NR at 12:42 hrs_19.06.2024 |  | Event-1 : 1235 MW Load Loss in Chhatisgarh at 05:30 hrs_03.04.2024 |  | Event-2: 4870 MW RE Gen Loss and 628 MW Load shedding at 11:24 hrs_06.04.2024 |  | Event-3: 1040 MW Rajasthan RE Gen loss at 10:28 hrs_19.04.2024 |  | Event-4: 1800 MW Gen Loss in APML Tiroda at 20:15 hrs_23.04.2024 |  | Event-1 : 1235 MW Load Loss in Chhatisgarh at 05:30 hrs_03.04.2024 |  | Event-2: 4870 MW RE Gen Loss and 628 MW Load shedding at 11:24 hrs_06.04.2024 |  | Event-3: 1040 MW Rajasthan RE Gen loss at 10:28 hrs_19.04.2024 |  | Event-4: 1800 MW Gen Loss in APML Tiroda at 20:15 hrs_23.04.2024 |  | Event-1 : 1235 MW Load Loss in Chhatisgarh at 05:30 hrs_03.04.2024 |  | Event-2: 4870 MW RE Gen Loss and 628 MW Load shedding at 11:24 hrs_06.04.2024 |  | Event-3: 1040 MW Rajasthan RE Gen loss at 10:28 hrs_19.04.2024 |  | Event-4: 1800 MW Gen Loss in APML Tiroda at 20:15 hrs_23.04.2024 |  | Event-1 : 1235 MW Load Loss in Chhatisgarh at 05:30 hrs_03.04.2024 |  | Event-2: 4870 MW RE Gen Loss and 628 MW Load shedding at 11:24 hrs_06.04.2024 |  | Event-3: 1040 MW Rajasthan RE Gen loss at 10:28 hrs_19.04.2024 |  | Event-4: 1800 MW Gen Loss in APML Tiroda at 20:15 hrs_23.04.2024 |  | Event-1 : 1235 MW Load Loss in Chhatisgarh at 05:30 hrs_03.04.2024 |  | Event-2: 4870 MW RE Gen Loss and 628 MW Load shedding at 11:24 hrs_06.04.2024 |  | Event-3: 1040 MW Rajasthan RE Gen loss at 10:28 hrs_19.04.2024 |  | Event-4: 1800 MW Gen Loss in APML Tiroda at 20:15 hrs_23.04.2024
|  |  | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | RLDC HDR Data (10 sec or better resolution) USING GEN UNIT DATA | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | RLDC HDR Data (10 sec or better resolution) GEN UNIT DATA | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | RLDC HDR Data (10 sec or better resolution) GEN UNIT DATA | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | RLDC HDR Data (10 sec or better resolution) GEN UNIT DATA @rldc END | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | RLDC HDR Data (10 sec or better resolution) GEN UNIT DATA | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station
1 | Actual Net Interchange before the Event, PA (Import +ve / Export -ve) | MW | -1113.2352 | -1174.5631 | -1211.209 | -1300.242 | -1269.4799 | -1359.5104 | -1514.1072 | DATA NOT RECEIVED | -882.5526 | DATA NOT RECEIVED | -269.1806 | DATA NOT RECEIVED | -262.7369 | DATA NOT RECEIVED | -412.6114 | -439.4642 | 0 | DATA NOT RECEIVED | -266.7578 | DATA NOT RECEIVED | -690.4008 | DATA NOT RECEIVED | -697.2928 | DATA NOT RECEIVED | -664.3309 | DATA NOT RECEIVED | -678.9511 | DATA NOT RECEIVED | -510.0974 | DATA NOT RECEIVED | -972.0436 | -1049.5493 | -1050.0299 | -1133.6323 | -1221.7202 | DATA NOT RECEIVED | -1266.0809 | -1335.3144 | -1354.6002 | -1480.4139 | -595.2853 | -656.8 | -568.1321 | -631.33 | -628.4 | -614.4067 | -578.1 | -689.9141 | -691.4 | -634.2516 | DATA NOT RECEIVED | -757.377 | -843.5 | -765.2736 | -836 | -432.5106 | -490.691 | -1241.2693 | -1312.3 | -742.5994 | -812 | -727.4088 | -780.5548 | -713.0139 | -758.5233 | -705.3262 | -738.4715 | -1197.8129 | -1145 | -722.5133 | -765.84 | -647.2273 | DATA NOT RECEIVED | -649.9367 | -698.9373 | -658.3722 | -706.7872 | -649.4374 | -1044 | -657.2186 | DATA NOT RECEIVED | -993.0785 | -1027.3789 | -979.3392 | -1013.4491 | -923.3915 | -957.516 | -1006.8722 | -1041.1258 | -589.9217 | -613.1118 | -242.6909 | -264.9533 | -243.1133 | -265.1907 | -495.3186 | -528.1282 | -489.8172 | -524.6574 | -487.4436 | -520.5319 | -1127.7998 | -1189.0001 | -1189.648 | -1137.5005 | -1198.4307 | -1145.1997 | -1206.437 | -1136.4993 | -1193.3374 | -1126.8008 | -1186.4688 | -851.9594 | DATA NOT RECEIVED | -841.5761 | DATA NOT RECEIVED | -853.4472 | DATA NOT RECEIVED | -881.3574 | DATA NOT RECEIVED | -488.7278 | DATA NOT RECEIVED | -45.0701 | DATA NOT RECEIVED | -45.0013 | DATA NOT RECEIVED | -32.0759 | DATA NOT RECEIVED | -106.8702 | DATA NOT RECEIVED | -106.8701 | DATA NOT RECEIVED | -1724.0713 | -1958.6938 | -1728.7849 | -1787.2647 | -1500.8807 | DATA NOT RECEIVED | -1889.7537 | -1972.6515 | -1051.5125 | -1124.2275 | -750.2456 | -791.6412 | -739.4709 | -781.0364 | -771.1437 | -811.4871 | -751.0817 | -797.0547 | -735.2957 | -789.2761 | -629.5228 | -662.9509 | -660.5961 | -622.0389 | -656.6714 | -654.3276 | -1284.7737 | -1325.6545 | -1325.8989 | -1276.8375 | -1318.0887 | -1270.3898 | DATA NOT RECEIVED
2 | Actual Net Interchange after the Event, PB (Import +ve / Export -ve) | MW | -1131.9792 | -1203.4162 | -1242.6672 | -1308.9088 | -1272.8049 | -1365.5521 | -1471.3176 |  | -935.383 |  | -270.0758 |  | -261.6783 |  | -407.1057 | -438.7519 | 0 |  | -280.8203 |  | -697.1116 |  | -700.0117 |  | -663.5357 |  | -654.1845 |  | -506.7795 |  | -1006.1964 | -1071.0844 | -1098.8757 | -1164.1279 | -1229.7159 |  | -1236.3657 | -1315.8063 | -1361.5393 | -1437.4292 | -594.7432 | -646.7 | -568.1321 | -638.7827 | -632.5 | -611.7937 | -575.9 | -684.7703 | -693 | -637.2356 |  | -759.4517 | -843.7 | -760.8021 | -843 | -434.198 | -497.3894 | -1241.2693 | -1282.7 | -773.8124 | -843 | -742.0443 | -777.2167 | -717.0637 | -756.3698 | -699.5637 | -738.051 | -1197.8129 | -1208 | -726.942 | -776.97 | -655.7047 |  | -666.9439 | -715.0417 | -658.2993 | -705.479 | -633.384 | -1031 | -670.3564 |  | -990.5424 | -1025.5519 | -966.4621 | -999.9074 | -933.3568 | -967.3078 | -1000.9454 | -1034.0892 | -614.5748 | -639.1816 | -242.2368 | -264.5344 | -246.1836 | -267.6482 | -493.773 | -525.9468 | -475.8111 | -509.3405 | -496.111 | -529.2888 | -1127.7998 | -1188.0011 | -1190.5415 | -1135.5994 | -1195.8244 | -1143.8987 | -1204.2348 | -1134.5991 | -1194.5741 | -1125.8038 | -1186.0472 | -867.2581 |  | -872.6938 |  | -853.2468 |  | -851.1371 |  | -524.954 |  | -44.8637 |  | -44.9325 |  | -32.0073 |  | -102.1003 |  | -106.7319 |  | -1707.801 | -2013.3659 | -1728.7849 | -1773.8592 | -1554.5728 |  | -1811.4114 | -1896.049 | -1111.0043 | -1189.4474 | -753.6437 | -798.5076 | -739.8812 | -785.08 | -766.6136 | -805.3937 | -707.6237 | -754.2013 | -752.6703 | -801.9409 | -629.5228 | -664.1505 | -660.5577 | -622.0389 | -659.0831 | -655.4814 | -1284.7737 | -1327.1034 | -1325.6316 | -1225.2543 | -1249.3989 | -1269.9219
3 | Change in net interchange, PB-PA (2 - 1) | MW | -18.744 | -28.8531 | -31.4583 | -8.6668 | -3.3251 | -6.0417 | 42.7896 |  | -52.8304 |  | -0.89517 |  | 1.0586 |  | 5.5057 | 0.71236 | 0 |  | -14.0625 |  | -6.7108 |  | -2.7189 |  | 0.79523 |  | 24.7666 |  | 3.3179 |  | -34.1528 | -21.5351 | -48.8458 | -30.4956 | -7.9957 |  | 29.7152 | 19.5081 | -6.9391 | 42.9847 | 0.54211 | 10.1 | 0 | -7.4528 | -4.1 | 2.613 | 2.2 | 5.1437 | -1.6 | -2.9839 |  | -2.0748 | -0.2 | 4.4714 | -6.3 | -1.6874 | -6.6985 | 0 | 29.6 | -31.213 | -31.2 | -14.6355 | 3.3381 | -4.0499 | 2.1535 | 5.7625 | 0.4205 | 0 | -63.8 | -4.4287 | -11.1 | -8.4774 |  | -17.0072 | -16.1044 | 0.072876 | 1.3082 | 16.0533 | 13 | -13.1378 |  | 2.5361 | 1.827 | 12.8771 | 13.5417 | -9.9652 | -9.7918 | 5.9268 | 7.0366 | -24.6531 | -26.0698 | 0.45409 | 0.4189 | -3.0704 | -2.4575 | 1.5456 | 2.1814 | 14.0061 | 15.3169 | -8.6674 | -8.7569 | 0 | 0.99902 | -0.8935 | 1.9011 | 2.6063 | 1.301 | 2.2022 | 1.9001 | -1.2367 | 0.99695 | 0.4216 | -15.2987 |  | -31.1177 |  | 0.20044 |  | 30.2202 |  | -36.2262 |  | 0.20634 |  | 0.068779 |  | 0.0686 |  | 4.77 |  | 0.13824 |  | 16.2703 | -54.6721 | 0 | 13.4055 | -53.692 |  | 78.3423 | 76.6025 | -59.4918 | -65.2199 | -3.3981 | -6.8664 | -0.41034 | -4.0436 | 4.5302 | 6.0934 | 43.458 | 42.8535 | -17.3746 | -12.6647 | 0 | -1.1996 | 0.0384 | 0 | -2.4117 | -1.1538 | 0 | -1.4489 | 0.2673 | 51.5833 | 68.6898 | 0.4679
4 | Generation Loss (+) / Load Throw off (-) during the Event, PL | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | PLANT OUT | [7 empty] | PLANT OUT
5 | Control Area Response, ΔP=(PB-PA) – PL (3-4) | MW | -18.744 | -28.8531 | -31.4583 | -8.6668 | -3.3251 | -6.0417 | 42.7896 |  | -52.8304 |  | -0.89517 |  | 1.0586 |  | 5.5057 | 0.71236 | 0 |  | -14.0625 |  | -6.7108 |  | -2.7189 |  | 0.79523 |  | 24.7666 |  | 3.3179 |  | -34.1528 | -21.5351 | -48.8458 | -30.4956 | -7.9957 |  | 29.7152 | 19.5081 | -6.9391 | 42.9847 | 0.54211 | 10.1 | 0 | -7.4528 | -4.1 | 2.613 | 2.2 | 5.1437 | -1.6 | -2.9839 |  | -2.0748 | -0.2 | 4.4714 | -6.3 | -1.6874 | -6.6985 | 0 | 29.6 | -31.213 | -31.2 | -14.6355 | 3.3381 | -4.0499 | 2.1535 | 5.7625 | 0.4205 | 0 | -63.8 | -4.4287 | -11.1 | -8.4774 |  | -17.0072 | -16.1044 | 0.072876 | 1.3082 | 16.0533 | 13 | -13.1378 |  | 2.5361 | 1.827 | 12.8771 | 13.5417 | -9.9652 | -9.7918 | 5.9268 | 7.0366 | -24.6531 | -26.0698 | 0.45409 | 0.4189 | -3.0704 | -2.4575 | 1.5456 | 2.1814 | 14.0061 | 15.3169 | -8.6674 | -8.7569 | 0 | 0.99902 | -0.8935 | 1.9011 | 2.6063 | 1.301 | 2.2022 | 1.9001 | -1.2367 | 0.99695 | 0.4216 | -15.2987 |  | -31.1177 |  | 0.20044 |  | 30.2202 |  | -36.2262 |  | 0.20634 |  | 0.068779 |  | 0.0686 |  | 4.77 |  | 0.13824 |  | 16.2703 | -54.6721 | 0 | 13.4055 | -53.692 |  | 78.3423 | 76.6025 | -59.4918 | -65.2199 | -3.3981 | -6.8664 | -0.41034 | -4.0436 | 4.5302 | 6.0934 | 43.458 | 42.8535 | -17.3746 | -12.6647 | 0 | -1.1996 | 0.0384 | 0 | -2.4117 | -1.1538 | 0 | -1.4489 | 0.2673 | 51.5833 | 68.6898 | 0.4679
6 | Frequency before the Event, fA | HZ | 50.071 | 50.071 | 50.073 | 50.073 | 49.929 | 49.929 | 50.034 |  | 50.06 |  | 50.071 |  | 50.073 |  | 49.929 | 49.929 | 50.034 |  | 50.06 |  | 50.071 |  | 50.073 |  | 49.929 |  | 50.034 |  | 50.06 |  | 50.071 | 50.071 | 50.073 | 50.073 | 49.929 |  | 50.034 | 50.034 | 50.06 | 50.06 | 50.071 | 50.071 | 50.073 | 50.073 | 50.073 | 49.929 | 49.929 | 50.034 | 50.034 | 50.06 |  | 50.071 | 50.071 | 50.073 | 50.073 | 49.929 | 49.929 | 50.034 | 50.034 | 50.06 | 50.06 | 50.071 | 50.071 | 50.073 | 50.073 | 49.929 | 49.929 | 50.034 | 50.034 | 50.06 | 50.06 | 50.071 |  | 50.073 | 50.073 | 49.929 | 49.929 | 50.034 | 50.034 | 50.06 |  | 50.071 | 50.071 | 50.073 | 50.073 | 49.929 | 49.929 | 50.034 | 50.034 | 50.06 | 50.06 | 50.071 | 50.071 | 50.073 | 50.073 | 49.929 | 49.929 | 50.034 | 50.034 | 50.06 | 50.06 | 50.071 | 50.071 | 50.071 | 50.073 | 50.073 | 49.929 | 49.929 | 50.034 | 50.034 | 50.06 | 50.06 | 50.071 |  | 50.073 |  | 49.929 |  | 50.034 |  | 50.06 |  | 50.071 |  | 50.073 |  | 49.929 |  | 50.034 |  | 50.06 |  | 50.071 | 50.071 | 50.073 | 50.073 | 49.929 |  | 50.034 | 50.034 | 50.06 | 50.06 | 50.071 | 50.071 | 50.073 | 50.073 | 49.929 | 49.929 | 50.034 | 50.034 | 50.06 | 50.06 | 50.071 | 50.071 | 50.071 | 50.073 | 50.073 | 50.073 | 49.929 | 49.929 | 49.929 | 50.034 | 50.034 | 50.06 | [17 empty] | 49.959 |  | 50.033 |  | 50.058 |  | 50.058 |  | 49.959 |  | 50.033 |  | 50.058 |  | 50.058 |  | 49.959 |  | 50.033 |  | 50.058 |  | 50.058
7 | Frequency after the Event, fB | HZ | 49.995 | 49.995 | 50.021 | 50.021 | 50.006 | 50.006 | 50.629 |  | 49.873 |  | 49.995 |  | 50.021 |  | 50.006 | 50.006 | 50.629 |  | 49.873 |  | 49.995 |  | 50.021 |  | 50.006 |  | 50.629 |  | 49.873 |  | 49.995 | 49.995 | 50.021 | 50.021 | 50.006 |  | 50.629 | 50.629 | 49.873 | 49.873 | 49.995 | 49.995 | 50.021 | 50.021 | 50.021 | 50.006 | 50.006 | 50.629 | 50.629 | 49.873 |  | 49.995 | 49.995 | 50.021 | 50.021 | 50.006 | 50.006 | 50.629 | 50.629 | 49.873 | 49.873 | 49.995 | 49.995 | 50.021 | 50.021 | 50.006 | 50.006 | 50.629 | 50.629 | 49.873 | 49.873 | 49.995 |  | 50.021 | 50.021 | 50.006 | 50.006 | 50.629 | 50.629 | 49.873 |  | 49.995 | 49.995 | 50.021 | 50.021 | 50.006 | 50.006 | 50.629 | 50.629 | 49.873 | 49.873 | 49.995 | 49.995 | 50.021 | 50.021 | 50.006 | 50.006 | 50.629 | 50.629 | 49.873 | 49.873 | 49.995 | 49.995 | 49.995 | 50.021 | 50.021 | 50.006 | 50.006 | 50.629 | 50.629 | 49.873 | 49.873 | 49.995 |  | 50.021 |  | 50.006 |  | 50.629 |  | 49.873 |  | 49.995 |  | 50.021 |  | 50.006 |  | 50.629 |  | 49.873 |  | 49.995 | 49.995 | 50.021 | 50.021 | 50.006 |  | 50.629 | 50.629 | 49.873 | 49.873 | 49.995 | 49.995 | 50.021 | 50.021 | 50.006 | 50.006 | 50.629 | 50.629 | 49.873 | 49.873 | 49.995 | 49.995 | 49.995 | 50.021 | 50.021 | 50.021 | 50.006 | 50.006 | 50.006 | 50.629 | 50.629 | 49.873 | [17 empty] | 50.024 |  | 49.766 |  | 50.006 |  | 49.974 |  | 50.024 |  | 49.766 |  | 50.006 |  | 49.974 |  | 50.024 |  | 49.766 |  | 50.006 |  | 49.974
8 | Change in Frequency, Δf=(fB-fA) (7-6) | HZ | -0.076 | -0.076 | -0.052 | -0.052 | 0.077 | 0.077 | 0.595 |  | -0.187 |  | -0.076 |  | -0.052 |  | 0.077 | 0.077 | 0.595 |  | -0.187 |  | -0.076 |  | -0.052 |  | 0.077 |  | 0.595 |  | -0.187 |  | -0.076 | -0.076 | -0.052 | -0.052 | 0.077 |  | 0.595 | 0.595 | -0.187 | -0.187 | -0.076 | -0.076 | -0.052 | -0.052 | -0.052 | 0.077 | 0.077 | 0.595 | 0.595 | -0.187 |  | -0.076 | -0.076 | -0.052 | -0.05 | 0.077 | 0.077 | 0.595 | 0.595 | -0.187 | -0.19 | -0.076 | -0.076 | -0.052 | -0.052 | 0.077 | 0.077 | 0.595 | 0.59 | -0.187 | -0.19 | -0.076 |  | -0.052 | -0.052 | 0.077 | 0.077 | 0.595 | 0.59 | -0.187 |  | -0.076 | -0.076 | -0.052 | -0.052 | 0.077 | 0.077 | 0.595 | 0.595 | -0.187 | -0.187 | -0.076 | -0.076 | -0.052 | -0.052 | 0.077 | 0.077 | 0.595 | 0.595 | -0.187 | -0.187 | -0.076 | -0.076 | -0.076 | -0.052 | -0.052 | 0.077 | 0.077 | 0.595 | 0.595 | -0.187 | -0.187 | -0.076 |  | -0.052 |  | 0.077 |  | 0.595 |  | -0.187 |  | -0.076 |  | -0.052 |  | 0.077 |  | 0.595 |  | -0.187 |  | -0.076 | -0.076 | -0.052 | -0.052 | 0.077 |  | 0.595 | 0.595 | -0.187 | -0.187 | -0.076 | -0.076 | -0.052 | -0.052 | 0.077 | 0.077 | 0.595 | 0.595 | -0.187 | -0.187 | -0.076 | -0.076 | -0.076 | -0.052 | -0.052 | -0.052 | 0.077 | 0.077 | 0.077 | 0.595 | 0.595 | -0.187 | [17 empty] | 0.065 |  | -0.267 |  | -0.052 |  | -0.084 |  | 0.065 |  | -0.267 |  | -0.052 |  | -0.084 |  | 0.065 |  | -0.267 |  | -0.052 |  | -0.084
9 | Frequency Response Characteristic, ΔP/ Δf (5 / 8) | MW/Hz | 246.6318 | 379.646 | 604.9664 | 166.6689 | -43.1828 | -78.4631 | 71.9152 |  | 282.5157 |  | 11.7786 |  | -20.3576 |  | 71.5023 | 9.2515 | 0 |  | 75.2005 |  | 88.2994 |  | 52.286 |  | 10.3276 |  | 41.6245 |  | -17.7426 |  | 449.3794 | 283.3566 | 939.3428 | 586.4538 | -103.8406 |  | 49.9415 | 32.7867 | 37.1074 | -229.8647 | -7.1331 | -132.8947 | 0 | 143.3229 | 78.8462 | 33.9355 | 28.5714 | 8.6449 | -2.6891 | 15.9569 |  | 27.2996 | 2.6316 | -85.9891 | 121 | -21.914 | -86.993 | 0 | 49.7479 | 166.9145 | 167 | 192.5723 | -43.9224 | 77.882 | -41.4129 | 74.8378 | 5.4611 | 0 | -107 | 23.6829 | 59 | 111.545 |  | 327.0616 | 309.7 | 0.94644 | 16.9896 | 26.9804 | 22 | 70.2557 |  | -33.3694 | -24.0394 | -247.6361 | -260.4173 | -129.4183 | -127.1664 | 9.9609 | 11.8262 | 131.8346 | 139.4109 | -5.9748 | -5.5118 | 59.0456 | 47.2596 | 20.0726 | 28.3299 | 23.5396 | 25.7427 | 46.3497 | 46.8283 | 0 | -13.145 | 11.7566 | -36.5601 | -50.1212 | 16.8964 | 28.6 | 3.1935 | -2.0785 | -5.3313 | -2.2545 | 201.2988 |  | 598.418 |  | 2.6031 |  | 50.7903 |  | 193.723 |  | -2.7151 |  | -1.3227 |  | 0.89091 |  | 8.0167 |  | -0.73924 |  | -214.0824 | 719.3697 | 0 | -257.7981 | -697.2989 |  | 131.6677 | 128.7437 | 318.1381 | 348.7695 | 44.7115 | 90.3473 | 7.8911 | 77.7611 | 58.8331 | 79.1356 | 73.0387 | 72.0226 | 92.9122 | 67.7259 | 0 | 15.7848 | -0.50526 | 0 | 46.3797 | 22.1885 | 0 | -18.8163 | 3.4714 | 86.6945 | 115.445 | -2.5021
10 | Frequency Response Obligation (FRO) of each control area | MW/Hz | 70.5703 | 70.5703 | 70.5703 | 70.5703 | 70.5703 | 70.5703 | 70.5703 |  | 70.5703 |  | 26.2492 |  | 26.2492 |  | 26.2492 | 26.2492 | 26.2492 |  | 26.2492 |  | 35.4067 |  | 35.4067 |  | 35.4067 |  | 35.4067 |  | 35.4067 |  | 72.6405 | 72.6405 | 72.6405 | 72.6405 | 72.6405 |  | 72.6405 | 72.6405 | 72.6405 | 72.6405 | 54.3898 | 54.3898 | 54.3898 | 54.3898 | 54.3898 | 54.3898 | 54.3898 | 54.3898 | 54.3898 | 54.3898 |  | 42.8225 | 42.8225 | 42.8225 | 43 | 42.8225 | 42.8225 | 42.8225 | 42.8225 | 42.8225 | 43 | 58.1913 | 58.1913 | 58.1913 | 58.1913 | 58.1913 | 58.1913 | 58.1913 | 58 | 58.1913 | 58 | 37.5454 |  | 37.5454 | 37.5454 | 37.5454 | 37.5454 | 37.5454 | 38 | 37.5454 |  | 53.179 | 53.179 | 53.179 | 53.179 | 53.179 | 53.179 | 53.179 | 53.179 | 53.179 | 53.179 | 24.3789 | 24.3789 | 24.3789 | 24.3789 | 24.3789 | 24.3789 | 24.3789 | 24.3789 | 24.3789 | 24.3789 | 59.5735 | 59.5735 | 59.5735 | 59.5735 | 59.5735 | 59.5735 | 59.5735 | 59.5735 | 59.5735 | 59.5735 | 59.5735 | 46.3904 |  | 46.3904 |  | 46.3904 |  | 46.3904 |  | 46.3904 |  | 4.1895 |  | 4.1895 |  | 4.1895 |  | 4.1895 |  | 4.1895 |  | 105.6464 | 105.6464 | 105.6464 | 105.6464 | 105.6464 |  | 105.6464 | 105.6464 | 105.6464 | 105.6464 | 83.2963 | 83.2963 | 83.2963 | 83.2963 | 83.2963 | 83.2963 | 83.2963 | 83.2963 | 83.2963 | 83.2963 | 37.8559 | 37.8559 | 37.8559 | 37.8559 | 37.8559 | 37.8559 | 37.8559 | 37.8559 | 37.8559 | 37.8559 | 37.8559 | 37.8559
11 | Frequency Response Performance (FRP) (9/10) |  | 3.4948 | 5.3797 | 8.5725 | 2.3617 | -0.61191 | -1.1118 | 1.0191 |  | 4.0033 |  | 0.44872 |  | -0.77555 |  | 2.724 | 0.35245 | 0 |  | 2.8649 |  | 2.4939 |  | 1.4767 |  | 0.29169 |  | 1.1756 |  | -0.50111 |  | 6.1863 | 3.9008 | 12.9314 | 8.0734 | -1.4295 |  | 0.68752 | 0.45136 | 0.51084 | -3.1644 | -0.13115 | -2.4434 | 0 | 2.6351 | 1.4497 | 0.62393 | 0.52531 | 0.15894 | -0.049441 | 0.29338 |  | 0.63751 | 0.061453 | -2.008 | 2.8187 | -0.51174 | -2.0315 | 0 | 1.1617 | 3.8978 | 3.8962 | 3.3093 | -0.75479 | 1.3384 | -0.71167 | 1.2861 | 0.093847 | 0 | -1.84 | 0.40698 | 1.02 | 2.9709 |  | 8.7111 | 8.2487 | 0.025208 | 0.45251 | 0.71861 | 0.58 | 1.8712 |  | -0.62749 | -0.45205 | -4.6567 | -4.897 | -2.4336 | -2.3913 | 0.18731 | 0.22239 | 2.4791 | 2.6215 | -0.24508 | -0.22609 | 2.422 | 1.9385 | 0.82336 | 1.1621 | 0.96557 | 1.0559 | 1.9012 | 1.9209 | 0 | -0.22065 | 0.19735 | -0.6137 | -0.84133 | 0.28362 | 0.48008 | 0.053606 | -0.034889 | -0.089491 | -0.037845 | 4.3392 |  | 12.8996 |  | 0.056113 |  | 1.0948 |  | 4.1759 |  | -0.64807 |  | -0.31571 |  | 0.21265 |  | 1.9135 |  | -0.17645 |  | -2.0264 | 6.8092 | 0 | -2.4402 | -6.6003 |  | 1.2463 | 1.2186 | 3.0113 | 3.3013 | 0.53678 | 1.0846 | 0.094736 | 0.93355 | 0.70631 | 0.95005 | 0.87685 | 0.86466 | 1.1154 | 0.81307 | 0 | 0.41697 | -0.013347 | 0 | 1.2252 | 0.58613 | 0 | -0.49705 | 0.091701 | 2.2901 | 3.0496 | -0.066096
Consideration of FRP for computation of Average Monthly FRP, Beta ‘ß’ |  |  | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 0.44 | 0 | 0 | 0 | 1 | 0.35 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0.29 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0.68 | 0.45 | 0.51 | 0 | 0 | 0 | 0 | 1 | 1 | 0.62 | 0.52 | 0.15 | 0 | 0.29 | 0 | 0.63 | 0.06 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0.09 | 0 | 0 | 0.4 | 1 | 1 | 0 | 1 | 1 | 0.02 | 0.45 | 0.71 | 0.58 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18 | 0.22 | 1 | 1 | 0 | 0 | 1 | 1 | 0.82 | 1 | 0.96 | 1 | 1 | 1 | 0 | 0 | 0.19 | 0 | 0 | 0.28 | 0.48 | 0.05 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0.05 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.53 | 1 | 0.09 | 0.93 | 0.7 | 0.95 | 0.87 | 0.86 | 1 | 0.81 | 0 | 0.41 | 0 | 0 | 1 | 0.58 | 0 | 0 | 0.09 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Average Monthly Frequency Response Performance, Beta ‘ß’ for April, 2024 | [10 empty] | 0.8 | 0.8 | [6 empty] | plant out |  | 0.61 | 0.4475 | [8 empty] | 0.658 | 0.65834 | [8 empty] | 0.638 | 0.49 |  |  | DATA FREEZE | [6 empty] | 0.412 | 0.362 | [6 empty] | data freeze |  | 0.326 | 0.612 | [6 empty] | data freeze |  | 0.68 | 0.218 | [8 empty] | 0.746 | 0.806 | [8 empty] | 0.236 | 0.244 | [8 empty] | 0.756 | 0.8 | DATA FREEZE | [8 empty] | 0.066 | 0.134 | [8 empty] | 0.81 | 0.81 | [8 empty] | 0.242 | 0.24253 |  |  | DATA FREEZE | [5 empty] | 0.4 | 0.6 | [8 empty] | 0.638 | 0.91 |  |  |  | DATA FREEZE |  |  | DATA FREEZE |  |  |  |  | 0.482 | 0.334
| IN CASE OF NON AVALABLITY OF GEN FRP,SCADA FRP HAS BEEN USED FOR CALCULATING AVERAGE FRP | [9 empty] | SCADA FRP | GEN FRP | [8 empty] | SCADA FRP | GEN FRP | [8 empty] | SCADA FRP | GEN FRP | [8 empty] | SCADA FRP | GEN FRP | [9 empty] | SCADA FRP | GEN FRP | [8 empty] | SCADA FRP | GEN FRP | [8 empty] | SCADA FRP | GEN FRP | [8 empty] | SCADA FRP | GEN FRP | [8 empty] | SCADA FRP | GEN FRP | [8 empty] | SCADA FRP | GEN FRP | [9 empty] | SCADA FRP(For event 3-genFRP taken) | GEN FRP | [8 empty] | SCADA FRP | GEN FRP | [8 empty] | SCADA FRP | GEN FRP | [8 empty] | SCADA FRP | GEN FRP | [8 empty] | SCADA FRP | GEN FRP | [11 empty] | SCADA FRP | GEN FRP
| Remarks(Given by ERLDC) | [52 empty] | -1
-1
[38 empty] | -1 |  | -1 | [48 empty] | -1 |  | -1 | [58 empty] | -1 |  | -1
| REMARKS | [20 empty] | EVENT 4 EXCLUDED DUE TO PLANT OUTAGE
| Beta for All events | [10 empty] | 0.8 | [9 empty] | 0.44 | [9 empty] | 0.65 | [9 empty] | 0.49 | [10 empty] | 0.36 | [9 empty] | 0.61 | [9 empty] | 0.21 | [9 empty] | 0.8 | [9 empty] | 0.24 | [9 empty] | 0.8 | [10 empty] | 0.13 | [9 empty] | 0.81 | [19 empty] | 0.6 | [9 empty] | 0.91 | [12 empty] | 0.33
| Beta classical events (E3,4,5) | [9 empty] | 0.66667 | [9 empty] | 0.675 | [9 empty] | 0.43 | [9 empty] | 0.15 | [10 empty] | 0.27333 | [9 empty] | 0.5 | [9 empty] | 0.36333 | [9 empty] | 0.67667 |  |  | -1 | [6 empty] | 0.40667 | [9 empty] | 1 | [10 empty] | 0.16 | [9 empty] | 0.68667 | [19 empty] | 0.6 | [9 empty] | 0.87333 | [12 empty] | 0.33333
Considerations for Beta Calculation
| IN CASE OF NON RECEIPT OF DATA, ERLDC SCADA DATA HAS BEEN USED TO CALCULATED AVERAGE BETA | [123 empty] | -1
IN CASE OF PLANT OUTAGE DURING ANY EVENT, THAT EVENT WILL BE EXCLUDED FROM BETA CALCULATION
IN CASE OF PLANT DATA FREEZE DURING ANY EVENT, ERLDC SCADA WLL BE USED FOR BETA CALCULATION
THE FRP VALUE & BETA WILL BE TRUNCATED TO 2 DECIMAL POINTS
If FRP for an event is less than or equal to 0, FRP (Event i) shall be equal to 0.
If FRP for an event lies between 0 to 1, FRP (Event i) shall be equal to the calculated value.
If FRP for an event is greater than or equal to 1, FRP (Event i) shall be equal to 1.

## May 24
|  |  | FSTPP I&II | [5 empty] | FSTPP III | [5 empty] | KhSTPP I | [5 empty] | KhSTPP II | [5 empty] | TSTPS-I | [5 empty] | BARH-1 | [5 empty] | BARH-2 | [5 empty] | GMR | [5 empty] | MPL | [5 empty] | Adhunik | [5 empty] | JITPL | [5 empty] | BRBCL | [5 empty] | Tashiding | [5 empty] | NPGC | [5 empty] | DARLIPALLI | [5 empty] | NORTH KARANPURA | [5 empty] | Teesta III | [5 empty] | Teesta V
S.No. | Particulars | Dimension | Event-1 : 1840 MW RE generation loss in Rajasthan at 14:41 hrs_02.05.2024 |  | Event-2: 1071 MW Gen Loss in Khedar(RGTPS) at 19:35 hrs_10.05.2024 |  | Event-3: 1587 MW Load Loss in Maharashtra (WR) at 17:59:38 hrs_28.05.2024 |  | Event-1 : 1840 MW RE generation loss in Rajasthan at 14:41 hrs_02.05.2024 |  | Event-2: 1071 MW Gen Loss in Khedar(RGTPS) at 19:35 hrs_10.05.2024 |  | Event-3: 1587 MW Load Loss in Maharashtra (WR) at 17:59:38 hrs_28.05.2024 |  | Event-1 : 1840 MW RE generation loss in Rajasthan at 14:41 hrs_02.05.2024 |  | Event-2: 1071 MW Gen Loss in Khedar(RGTPS) at 19:35 hrs_10.05.2024 |  | Event-3: 1587 MW Load Loss in Maharashtra (WR) at 17:59:38 hrs_28.05.2024 |  | Event-1 : 1840 MW RE generation loss in Rajasthan at 14:41 hrs_02.05.2024 |  | Event-2: 1071 MW Gen Loss in Khedar(RGTPS) at 19:35 hrs_10.05.2024 |  | Event-3: 1587 MW Load Loss in Maharashtra (WR) at 17:59:38 hrs_28.05.2024 |  | Event-1 : 1840 MW RE generation loss in Rajasthan at 14:41 hrs_02.05.2024 |  | Event-2: 1071 MW Gen Loss in Khedar(RGTPS) at 19:35 hrs_10.05.2024 |  | Event-3: 1587 MW Load Loss in Maharashtra (WR) at 17:59:38 hrs_28.05.2024 |  | Event-1 : 1840 MW RE generation loss in Rajasthan at 14:41 hrs_02.05.2024 |  | Event-2: 1071 MW Gen Loss in Khedar(RGTPS) at 19:35 hrs_10.05.2024 |  | Event-3: 1587 MW Load Loss in Maharashtra (WR) at 17:59:38 hrs_28.05.2024 |  | Event-1 : 1840 MW RE generation loss in Rajasthan at 14:41 hrs_02.05.2024 |  | Event-2: 1071 MW Gen Loss in Khedar(RGTPS) at 19:35 hrs_10.05.2024 |  | Event-3: 1587 MW Load Loss in Maharashtra (WR) at 17:59:38 hrs_28.05.2024 |  | Event-1 : 1840 MW RE generation loss in Rajasthan at 14:41 hrs_02.05.2024 |  | Event-2: 1071 MW Gen Loss in Khedar(RGTPS) at 19:35 hrs_10.05.2024 |  | Event-3: 1587 MW Load Loss in Maharashtra (WR) at 17:59:38 hrs_28.05.2024 |  | Event-1 : 1840 MW RE generation loss in Rajasthan at 14:41 hrs_02.05.2024 |  | Event-2: 1071 MW Gen Loss in Khedar(RGTPS) at 19:35 hrs_10.05.2024 |  | Event-3: 1587 MW Load Loss in Maharashtra (WR) at 17:59:38 hrs_28.05.2024 |  | Event-1 : 1840 MW RE generation loss in Rajasthan at 14:41 hrs_02.05.2024 |  | Event-2: 1071 MW Gen Loss in Khedar(RGTPS) at 19:35 hrs_10.05.2024 |  | Event-3: 1587 MW Load Loss in Maharashtra (WR) at 17:59:38 hrs_28.05.2024 |  | Event-1 : 1840 MW RE generation loss in Rajasthan at 14:41 hrs_02.05.2024 |  | Event-2: 1071 MW Gen Loss in Khedar(RGTPS) at 19:35 hrs_10.05.2024 |  | Event-3: 1587 MW Load Loss in Maharashtra (WR) at 17:59:38 hrs_28.05.2024 |  | Event-1 : 1840 MW RE generation loss in Rajasthan at 14:41 hrs_02.05.2024 |  | Event-2: 1071 MW Gen Loss in Khedar(RGTPS) at 19:35 hrs_10.05.2024 |  | Event-3: 1587 MW Load Loss in Maharashtra (WR) at 17:59:38 hrs_28.05.2024 |  | Event-1 : 1840 MW RE generation loss in Rajasthan at 14:41 hrs_02.05.2024 |  | Event-2: 1071 MW Gen Loss in Khedar(RGTPS) at 19:35 hrs_10.05.2024 |  | Event-3: 1587 MW Load Loss in Maharashtra (WR) at 17:59:38 hrs_28.05.2024 |  | Event-1 : 1840 MW RE generation loss in Rajasthan at 14:41 hrs_02.05.2024 |  | Event-2: 1071 MW Gen Loss in Khedar(RGTPS) at 19:35 hrs_10.05.2024 |  | Event-3: 1587 MW Load Loss in Maharashtra (WR) at 17:59:38 hrs_28.05.2024 |  | Event-1 : 1840 MW RE generation loss in Rajasthan at 14:41 hrs_02.05.2024 |  | Event-2: 1071 MW Gen Loss in Khedar(RGTPS) at 19:35 hrs_10.05.2024 |  | Event-3: 1587 MW Load Loss in Maharashtra (WR) at 17:59:38 hrs_28.05.2024 |  | Event-1 : 1840 MW RE generation loss in Rajasthan at 14:41 hrs_02.05.2024 |  | Event-2: 1071 MW Gen Loss in Khedar(RGTPS) at 19:35 hrs_10.05.2024 |  | Event-3: 1587 MW Load Loss in Maharashtra (WR) at 17:59:38 hrs_28.05.2024 |  | Event-1 : 1840 MW RE generation loss in Rajasthan at 14:41 hrs_02.05.2024 |  | Event-2: 1071 MW Gen Loss in Khedar(RGTPS) at 19:35 hrs_10.05.2024 |  | Event-3: 1587 MW Load Loss in Maharashtra (WR) at 17:59:38 hrs_28.05.2024 |  | Event-1 : 1840 MW RE generation loss in Rajasthan at 14:41 hrs_02.05.2024 |  | Event-2: 1071 MW Gen Loss in Khedar(RGTPS) at 19:35 hrs_10.05.2024 |  | Event-3: 1587 MW Load Loss in Maharashtra (WR) at 17:59:38 hrs_28.05.2024
|  |  | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data | RLDC SCADA Data | Generator High Resolution Data
1 | Actual Net Interchange before the Event, PA (Import +ve / Export -ve) | MW | -1380.3678 | DATA NOT RECEIVED | -1407.9408 | -1527.018 | -1066.5398 | DATA NOT RECEIVED | -401.4033 | DATA NOT RECEIVED | -469.5744 | -492.347 | -464.1389 | DATA NOT RECEIVED | -700.4717 | DATA NOT RECEIVED | -677.8807 | DATA NOT RECEIVED | -511.6617 | DATA NOT RECEIVED | -1364.9647 | -1448.271 | -835.5033 | -877.5606 | -1226.9799 | DATA NOT RECEIVED | -886.8405 | -955.3 | -892.5211 | -964.5 | -871.9539 | -948 | -432.8004 | DATA NOT RECEIVED | -1194.8629 | DATA NOT RECEIVED | -0.32024 | PLANT OUT | -516.333 | DATA NOT RECEIVED | -1239.597 | DATA NOT RECEIVED | -1154.8746 | DATA NOT RECEIVED | -614.5661 | -664.6113 | -659.2866 | -707.0728 | -629.8681 | -674.5546 | -1008.7201 | -1041.699 | -1002.847 | -1038.4711 | -991.874 | -1026.8259 | -483.0038 | -517 | -450.6346 | -485.2564 | -479.4973 | -514.6869 | -1094.1013 | -1149.218 | -1131.8997 | -1193.8692 | -1089.7013 | -1151.127 | -891.0132 | -959.5611 | -754.0134 | -947.0596 | -858.8723 | DATA NOT RECEIVED | -0.069127 | DATA NOT RECEIVED | 5.8741 | DATA NOT RECEIVED | 31.6601 | DATA NOT RECEIVED | -1856.3601 | -1937.104 | -1892.7671 | -1967.223 | -1801.2661 | -1879.3744 | -741.7609 | -802.7696 | -751.98 | -808.0656 | -741.7695 | -787.7224 | -647.0765 | -657.8541 | -1265.4049 | -1313.928 | -1193.2657 | -1879.3744 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2 | Actual Net Interchange after the Event, PB (Import +ve / Export -ve) | MW | -1397.3395 |  | -1436.2753 | -1549.797 | -1024.2474 |  | -427.9025 |  | -469.7303 | -490.9323 | -463.9044 |  | -703.9655 |  | -673.7775 |  | -511.5026 |  | -1371.2491 | -1451.1702 | -848.9377 | -891.4891 | -1230.7434 |  | -889.6366 | -962.1 | -897.1235 | -967.6 | -871.9573 | -950.4 | -435.9768 |  | -1194.7643 |  | -0.3198 |  | -514.7891 |  | -1233.4937 |  | -1150.7966 |  | -619.2353 | -665.5866 | -662.8284 | -708.0957 | -617.7581 | -663.8263 | -1011.3592 | -1044.944 | -1003.9171 | -1036.8987 | -993.6469 | -1026.3677 | -484.5001 | -521 | -449.6472 | -484.3767 | -471.0665 | -500.6521 | -1093.9969 | -1151.003 | -1136.3002 | -1194.6636 | -1089.7002 | -1151.508 | -899.9764 | -968.946 | -754.0134 | -939.4503 | -848.4312 |  | -0.069127 |  | 5.8741 |  | 31.659 |  | -1839.301 | -1916.382 | -1879.2334 | -1958.526 | -1738.9503 | -1808.8625 | -748.3657 | -808.5337 | -755.8336 | -811.6309 | -731.2786 | -779.2442 | -647.0765 | -661.2625 | -1271.8298 | -1311.689 | -1179.9027 | -1808.8625 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
3 | Change in net interchange, PB-PA (2 - 1) | MW | -16.9717 |  | -28.3345 | -22.779 | 42.2924 |  | -26.4992 |  | -0.15598 | 1.4147 | 0.23453 |  | -3.4938 |  | 4.1032 |  | 0.15912 |  | -6.2844 | -2.8992 | -13.4344 | -13.9285 | -3.7635 |  | -2.7961 | -6.8 | -4.6025 | -3.1 | -0.003479 | -2.4 | -3.1764 |  | 0.098633 |  | 0.0004355 |  | 1.5439 |  | 6.1034 |  | 4.078 |  | -4.6692 | -0.9753 | -3.5417 | -1.0229 | 12.11 | 10.7283 | -2.6391 | -3.245 | -1.0701 | 1.5725 | -1.7729 | 0.45821 | -1.4963 | -3.9 | 0.9873 | 0.8797 | 8.4308 | 14.0348 | 0.10437 | -1.785 | -4.4005 | -0.7944 | 0.0010986 | -0.381 | -8.9632 | -9.3849 | 0 | 7.6093 | 10.4411 |  | 0 |  | 0 |  | -0.0011063 |  | 17.0591 | 20.722 | 13.5337 | 8.697 | 62.3158 | 70.5119 | -6.6047 | -5.7641 | -3.8535 | -3.5653 | 10.491 | 8.4782 | 0 | -3.4084 | -6.4249 | 2.239 | 13.363 | 70.5119 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
4 | Generation Loss (+) / Load Throw off (-) during the Event, PL | MW | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
5 | Control Area Response, ΔP=(PB-PA) – PL (3-4) | MW | -16.9717 |  | -28.3345 | -22.779 | 42.2924 |  | -26.4992 |  | -0.15598 | 1.4147 | 0.23453 |  | -3.4938 |  | 4.1032 |  | 0.15912 |  | -6.2844 | -2.8992 | -13.4344 | -13.9285 | -3.7635 |  | -2.7961 | -6.8 | -4.6025 | -3.1 | -0.003479 | -2.4 | -3.1764 |  | 0.098633 |  | 0.0004355 |  | 1.5439 |  | 6.1034 |  | 4.078 |  | -4.6692 | -0.9753 | -3.5417 | -1.0229 | 12.11 | 10.7283 | -2.6391 | -3.245 | -1.0701 | 1.5725 | -1.7729 | 0.45821 | -1.4963 | -3.9 | 0.9873 | 0.8797 | 8.4308 | 14.0348 | 0.10437 | -1.785 | -4.4005 | -0.7944 | 0.0010986 | -0.381 | -8.9632 | -9.3849 | 0 | 7.6093 | 10.4411 |  | 0 |  | 0 |  | -0.0011063 |  | 17.0591 | 20.722 | 13.5337 | 8.697 | 62.3158 | 70.5119 | -6.6047 | -5.7641 | -3.8535 | -3.5653 | 10.491 | 8.4782 | 0 | -3.4084 | -6.4249 | 2.239 | 13.363 | 70.5119 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
6 | Frequency before the Event, fA | HZ | 50.024 |  | 49.986 | 49.986 | 50.091 |  | 50.024 |  | 49.986 | 49.986 | 50.091 |  | 50.024 |  | 49.986 |  | 50.091 |  | 50.024 | 50.024 | 49.986 | 49.986 | 50.091 |  | 50.024 | 50.024 | 49.986 | 49.986 | 50.091 | 50.091 | 50.024 |  | 49.986 |  | 50.091 |  | 50.024 |  | 49.986 |  | 50.091 |  | 50.024 | 50.024 | 49.986 | 49.986 | 50.091 | 50.091 | 50.024 | 50.024 | 49.986 | 49.986 | 50.091 | 50.091 | 50.024 | 50.024 | 49.986 | 49.986 | 50.091 | 50.091 | 50.024 | 50.024 | 49.986 | 49.986 | 50.091 | 50.091 | 50.024 | 50.024 | 49.986 | 49.986 | 50.091 |  | 50.024 |  | 49.986 |  | 50.091 |  | 50.024 | 50.024 | 49.986 | 49.986 | 50.091 | 50.091 | 50.024 | 50.024 | 49.986 | 49.986 | 50.091 | 50.091 | 50.024 | 50.024 | 49.986 | 49.986 | 50.091 | 50.091 | 50.024 |  | 49.986 |  | 50.091 |  | 50.024 |  | 49.986 |  | 50.091
7 | Frequency after the Event, fB | HZ | 49.983 |  | 49.941 | 49.941 | 50.14 |  | 49.983 |  | 49.941 | 49.941 | 50.14 |  | 49.983 |  | 49.941 |  | 50.14 |  | 49.983 | 49.983 | 49.941 | 49.941 | 50.14 |  | 49.983 | 49.983 | 49.941 | 49.941 | 50.14 | 50.14 | 49.983 |  | 49.941 |  | 50.14 |  | 49.983 |  | 49.941 |  | 50.14 |  | 49.983 | 49.983 | 49.941 | 49.941 | 50.14 | 50.14 | 49.983 | 49.983 | 49.941 | 49.941 | 50.14 | 50.14 | 49.983 | 49.983 | 49.941 | 49.941 | 50.14 | 50.14 | 49.983 | 49.983 | 49.941 | 49.941 | 50.14 | 50.14 | 49.983 | 49.983 | 49.941 | 49.941 | 50.14 |  | 49.983 |  | 49.941 |  | 50.14 |  | 49.983 | 49.983 | 49.941 | 49.941 | 50.14 | 50.14 | 49.983 | 49.983 | 49.941 | 49.941 | 50.14 | 50.14 | 49.983 | 49.983 | 49.941 | 49.941 | 50.14 | 50.14 | 49.983 |  | 49.941 |  | 50.14 |  | 49.983 |  | 49.941 |  | 50.14
8 | Change in Frequency, Δf=(fB-fA) (7-6) | HZ | -0.041 |  | -0.045 | -0.045 | 0.049 |  | -0.041 |  | -0.045 | -0.045 | 0.049 |  | -0.041 |  | -0.045 |  | 0.049 |  | -0.041 | -0.041 | -0.045 | -0.045 | 0.049 |  | -0.041 | -0.041 | -0.045 | -0.045 | 0.049 | 0.049 | -0.041 |  | -0.045 |  | 0.049 |  | -0.041 |  | -0.045 |  | 0.049 |  | -0.041 | -0.041 | -0.045 | -0.045 | 0.049 | 0.049 | -0.041 | -0.041 | -0.045 | -0.045 | 0.049 | 0.049 | -0.041 | -0.04 | -0.045 | -0.045 | 0.049 | 0.049 | -0.041 | -0.041 | -0.045 | -0.045 | 0.049 | 0.049 | -0.041 | -0.041 | -0.045 | -0.045 | 0.049 |  | -0.041 |  | -0.045 |  | 0.049 |  | -0.041 | -0.041 | -0.045 | -0.045 | 0.049 | 0.049 | -0.041 | -0.041 | -0.045 | -0.045 | 0.049 | 0.049 | -0.041 | -0.041 | -0.045 | -0.045 | 0.049 | 0.049 | -0.041 |  | -0.045 |  | 0.049 |  | -0.041 |  | -0.045 |  | 0.049
9 | Frequency Response Characteristic, ΔP/ Δf (5 / 8) | MW/Hz | 413.9434 |  | 629.6549 | 506.2 | 863.1094 |  | 646.3214 |  | 3.4661 | -31.4378 | 4.7863 |  | 85.214 |  | -91.1825 |  | 3.2473 |  | 153.2786 | 70.7122 | 298.5419 | 309.5222 | -76.8071 |  | 68.1986 | 165.8537 | 102.2773 | 68.8889 | -0.071 | -48.9796 | 77.473 |  | -2.1918 |  | 0.0088878 |  | -37.6557 |  | -135.631 |  | 83.2245 |  | 113.8827 | 23.7878 | 78.7055 | 22.7311 | 247.1438 | 218.9449 | 64.3683 | 79.1463 | 23.7793 | -34.9437 | -36.1826 | 9.3513 | 36.4946 | 96 | -21.9401 | -19.5489 | 172.0581 | 286.4245 | -2.5456 | 43.5366 | 97.7892 | 17.6533 | 0.022421 | -7.7755 | 218.6145 | 228.9 | 0 | -169.0956 | 213.0837 |  | 0 |  | 0 |  | -0.022577 |  | -416.0752 | -505.4146 | -300.7487 | -193.2667 | 1271.7509 | 1439.0184 | 161.0911 | 140.5878 | 85.6337 | 79.2289 | 214.1014 | 173.0245 | 0 | 83.1317 | 142.7762 | -49.7556 | 272.715 | 1439.0184 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
10 | Frequency Response Obligation (FRO) of each control area | MW/Hz | 70.5703 |  | 45.3666 | 45.3666 | 45.3666 |  | 26.2492 |  | 16.8745 | 16.8745 | 16.8745 |  | 35.4067 |  | 22.7614 |  | 22.7614 |  | 72.6405 | 72.6405 | 46.6975 | 46.6975 | 46.6975 |  | 54.3898 | 54.3898 | 34.9649 | 34.9649 | 34.9649 | 34.9649 | 42.8225 |  | 27.5288 |  | 27.5288 |  | 58.1913 |  | 37.4087 |  | 37.4087 |  | 37.5454 | 37.5454 | 24.1363 | 24.1363 | 24.1363 | 24.1363 | 53.179 | 53.179 | 34.1865 | 34.1865 | 34.1865 | 34.1865 | 24.3789 | 24 | 15.6721 | 15.6721 | 15.6721 | 15.6721 | 59.5735 | 59.5735 | 38.2973 | 38.2973 | 38.2973 | 38.2973 | 46.3904 | 46.3904 | 29.8224 | 29.8224 | 29.8224 |  | 4.1895 |  | 2.6932 |  | 2.6932 |  | 105.6464 | 105.6464 | 67.9155 | 67.9155 | 67.9155 | 67.9155 | 83.2963 | 83.2963 | 53.5476 | 53.5476 | 53.5476 | 53.5476 | 37.8559 | 37.8559 | 24.3359 | 24.3359 | 24.3359 | 67.9155 | 51.3606 |  | 33.0175 |  | 33.0175 |  | 27.8375 |  | 17.8955 |  | 17.8955
11 | Frequency Response Performance (FRP) (9/10) |  | 5.8657 |  | 13.8793 | 11.158 | 19.0252 |  | 24.6226 |  | 0.20541 | -1.863 | 0.28364 |  | 2.4067 |  | -4.006 |  | 0.14267 |  | 2.1101 | 0.97345 | 6.3931 | 6.6282 | -1.6448 |  | 1.2539 | 3.0494 | 2.9251 | 1.9702 | -0.0020306 | -1.4008 | 1.8092 |  | -0.07962 |  | PLANT OUT |  | -0.6471 |  | -3.6257 |  | 2.2247 |  | 3.0332 | 0.63358 | 3.2609 | 0.94178 | 10.2395 | 9.0712 | 1.2104 | 1.4883 | 0.69558 | -1.0221 | -1.0584 | 0.27354 | 1.497 | 3.93 | -1.3999 | -1.2474 | 10.9786 | 18.276 | -0.042731 | 0.7308 | 2.5534 | 0.46096 | 0.00058545 | -0.20303 | 4.7125 | 4.9342 | 0 | -5.6701 | 7.1451 |  | 0 |  | 0 |  | -0.0083828 |  | -3.9384 | -4.784 | -4.4283 | -2.8457 | 18.7255 | 21.1883 | 1.934 | 1.6878 | 1.5992 | 1.4796 | 3.9983 | 3.2312 | 0 | 2.196 | 5.8669 | -2.0445 | 11.2063 | 21.1883 | NA |  | NA |  | NA |  | NA |  | NA |  | NA
Consideration of FRP for computation of Average Monthly FRP, Beta ‘ß’ |  |  | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0.2 | 0 | 0.28 | 0 | 1 | 0 | 0 | 0 | 0.14 | 0 | 1 | 0.97 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0.63 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.69 | 0 | 0 | 0.27 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0.73 | 1 | 0.46 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Average Monthly Frequency Response Performance for May, 2024 | [5 empty] | 1 | 1 |  |  |  |  | 0.49333 | 0.42667 |  |  |  |  | 0.38 | 0.38 |  |  |  |  | 0.66667 | 0.65667 |  |  |  |  | 0.66667 | 0.66667 |  |  |  |  | 0.5 | 0.5 |  |  |  |  | 0.33333 | 0.33333 |  |  |  |  | 1 | 0.85667 |  |  |  |  | 0.56333 | 0.42333 |  |  |  |  | 0.66667 | 0.66667 |  |  |  |  | 0.33333 | 0.39667 |  |  |  |  | 0.66667 | 0.66667 |  |  |  |  | 0 | 0 |  |  |  |  | 0.33333 | 0.33333 |  |  |  |  | 1 | 1 |  |  |  |  | 0.66667 | 0.66667 | NA |  | NA |  | NA |  | NA |  | NA |  | NA
[7 empty] | SCADA FRP | GEN FRP |  |  |  |  | SCADA FRP | GEN FRP |  |  |  |  | SCADA FRP | GEN FRP |  |  |  |  | SCADA FRP | GEN FRP |  |  |  |  | SCADA FRP | GEN FRP |  |  |  |  | SCADA FRP | GEN FRP |  |  |  |  | SCADA FRP | GEN FRP |  |  |  |  | SCADA FRP | GEN FRP |  |  |  |  | SCADA FRP | GEN FRP |  |  |  |  | SCADA FRP | GEN FRP |  |  |  |  | SCADA FRP | GEN FRP |  |  |  |  | SCADA FRP | GEN FRP |  |  |  |  | SCADA FRP | GEN FRP |  |  |  |  | SCADA FRP | GEN FRP |  |  |  |  | SCADA FRP | GEN FRP |  |  |  |  | SCADA FRP | GEN FRP |  |  |  |  | SCADA FRP | GEN FRP |  |  |  |  | SCADA FRP | GEN FRP
[6 empty] | -1 | [5 empty] | -1 | [9 empty] | -1 | [7 empty] | -1 | [16 empty] | -1 |  |  |  |  | -1 | [7 empty] | -1 |  |  |  | -1 | [6 empty] | -1 | [12 empty] | -1 |  |  |  |  | -1 | [6 empty] | -1
| Remarks(Given by RLDC) | [29 empty] | Data freeze | [5 empty] | Plant out | [29 empty] | DATA FREEZE |  |  |  | DATA FREEZE |  |  |  | plant out |  | data freeze |  | data freeze | [13 empty] | Data freeze | [5 empty] | PLANT OUT | [5 empty] | PLANT OUT
| Beta for All events | [6 empty] | 1 | [5 empty] | 0.42 | [5 empty] | 0.38 | [5 empty] | 0.65 | [5 empty] | 0.66 | [5 empty] | 0.5 | [5 empty] | 0.33 | [5 empty] | 0.85 | [5 empty] | 0.42 | [5 empty] | 0.66 | [5 empty] | 0.39 | [5 empty] | 0.66 |  |  |  |  | N/A | [6 empty] | 0.33 | [5 empty] | 1 | [5 empty] | 0.66
Considerations for Beta Calculation
Considerations for Beta Calculation
IN CASE OF NON RECEIPT OF DATA, ERLDC SCADA DATA HAS BEEN USED TO CALCULATED AVERAGE BETA
IN CASE OF PLANT OUTAGE DURING ANY EVENT, THAT EVENT WILL BE EXCLUDED FROM BETA CALCULATION
IN CASE OF PLANT DATA FREEZE DURING ANY EVENT, ERLDC SCADA WLL BE USED FOR BETA CALCULATION
THE FRP VALUE & BETA WILL BE TRUNCATED TO 2 DECIMAL POINTS
If FRP for an event is less than or equal to 0, FRP (Event i) shall be equal to 0.
If FRP for an event lies between 0 to 1, FRP (Event i) shall be equal to the calculated value.
If FRP for an event is greater than or equal to 1, FRP (Event i) shall be equal to 1.

## April 24
|  |  | FSTPP I&II | [7 empty] | FSTPP III | [7 empty] | KhSTPP I | [7 empty] | KhSTPP II | [7 empty] | TSTPS-I | [7 empty] | BARH-1 | [7 empty] | BARH-2 | [7 empty] | GMR | [7 empty] | MPL | [7 empty] | Adhunik | [7 empty] | JITPL | [7 empty] | BRBCL | [7 empty] | Tashiding | [7 empty] | NPGC | [7 empty] | DARLIPALLI | [7 empty] | NORTH KARANPURA | [7 empty] | Teesta III | [7 empty] | Teesta V | [7 empty] | TALA | [7 empty] | CHUKHA | [7 empty] | Chujachen
S.No. | Particulars | Dimension | Event-1 : 1235 MW Load Loss in Chhatisgarh at 05:30 hrs_03.04.2024 |  | Event-2: 4870 MW RE Gen Loss and 628 MW Load shedding at 11:24 hrs_06.04.2024 |  | Event-3: 1040 MW Rajasthan RE Gen loss at 10:28 hrs_19.04.2024 |  | Event-4: 1800 MW Gen Loss in APML Tiroda at 20:15 hrs_23.04.2024 |  | Event-1 : 1235 MW Load Loss in Chhatisgarh at 05:30 hrs_03.04.2024 |  | Event-2: 4870 MW RE Gen Loss and 628 MW Load shedding at 11:24 hrs_06.04.2024 |  | Event-3: 1040 MW Rajasthan RE Gen loss at 10:28 hrs_19.04.2024 |  | Event-4: 1800 MW Gen Loss in APML Tiroda at 20:15 hrs_23.04.2024 |  | Event-1 : 1235 MW Load Loss in Chhatisgarh at 05:30 hrs_03.04.2024 |  | Event-2: 4870 MW RE Gen Loss and 628 MW Load shedding at 11:24 hrs_06.04.2024 |  | Event-3: 1040 MW Rajasthan RE Gen loss at 10:28 hrs_19.04.2024 |  | Event-4: 1800 MW Gen Loss in APML Tiroda at 20:15 hrs_23.04.2024 |  | Event-1 : 1235 MW Load Loss in Chhatisgarh at 05:30 hrs_03.04.2024 |  | Event-2: 4870 MW RE Gen Loss and 628 MW Load shedding at 11:24 hrs_06.04.2024 |  | Event-3: 1040 MW Rajasthan RE Gen loss at 10:28 hrs_19.04.2024 |  | Event-4: 1800 MW Gen Loss in APML Tiroda at 20:15 hrs_23.04.2024 |  | Event-1 : 1235 MW Load Loss in Chhatisgarh at 05:30 hrs_03.04.2024 |  | Event-2: 4870 MW RE Gen Loss and 628 MW Load shedding at 11:24 hrs_06.04.2024 |  | Event-3: 1040 MW Rajasthan RE Gen loss at 10:28 hrs_19.04.2024 |  | Event-4: 1800 MW Gen Loss in APML Tiroda at 20:15 hrs_23.04.2024 |  | Event-1 : 1235 MW Load Loss in Chhatisgarh at 05:30 hrs_03.04.2024 |  | Event-2: 4870 MW RE Gen Loss and 628 MW Load shedding at 11:24 hrs_06.04.2024 |  | Event-3: 1040 MW Rajasthan RE Gen loss at 10:28 hrs_19.04.2024 |  | Event-4: 1800 MW Gen Loss in APML Tiroda at 20:15 hrs_23.04.2024 |  | Event-1 : 1235 MW Load Loss in Chhatisgarh at 05:30 hrs_03.04.2024 |  | Event-2: 4870 MW RE Gen Loss and 628 MW Load shedding at 11:24 hrs_06.04.2024 |  | Event-3: 1040 MW Rajasthan RE Gen loss at 10:28 hrs_19.04.2024 |  | Event-4: 1800 MW Gen Loss in APML Tiroda at 20:15 hrs_23.04.2024 |  | Event-1 : 1235 MW Load Loss in Chhatisgarh at 05:30 hrs_03.04.2024 |  | Event-2: 4870 MW RE Gen Loss and 628 MW Load shedding at 11:24 hrs_06.04.2024 |  | Event-3: 1040 MW Rajasthan RE Gen loss at 10:28 hrs_19.04.2024 |  | Event-4: 1800 MW Gen Loss in APML Tiroda at 20:15 hrs_23.04.2024 |  | Event-1 : 1235 MW Load Loss in Chhatisgarh at 05:30 hrs_03.04.2024 |  | Event-2: 4870 MW RE Gen Loss and 628 MW Load shedding at 11:24 hrs_06.04.2024 |  | Event-3: 1040 MW Rajasthan RE Gen loss at 10:28 hrs_19.04.2024 |  | Event-4: 1800 MW Gen Loss in APML Tiroda at 20:15 hrs_23.04.2024 |  | Event-1 : 1235 MW Load Loss in Chhatisgarh at 05:30 hrs_03.04.2024 |  | Event-2: 4870 MW RE Gen Loss and 628 MW Load shedding at 11:24 hrs_06.04.2024 |  | Event-3: 1040 MW Rajasthan RE Gen loss at 10:28 hrs_19.04.2024 |  | Event-4: 1800 MW Gen Loss in APML Tiroda at 20:15 hrs_23.04.2024 |  | Event-1 : 1235 MW Load Loss in Chhatisgarh at 05:30 hrs_03.04.2024 |  | Event-2: 4870 MW RE Gen Loss and 628 MW Load shedding at 11:24 hrs_06.04.2024 |  | Event-3: 1040 MW Rajasthan RE Gen loss at 10:28 hrs_19.04.2024 |  | Event-4: 1800 MW Gen Loss in APML Tiroda at 20:15 hrs_23.04.2024 |  | Event-1 : 1235 MW Load Loss in Chhatisgarh at 05:30 hrs_03.04.2024 |  | Event-2: 4870 MW RE Gen Loss and 628 MW Load shedding at 11:24 hrs_06.04.2024 |  | Event-3: 1040 MW Rajasthan RE Gen loss at 10:28 hrs_19.04.2024 |  | Event-4: 1800 MW Gen Loss in APML Tiroda at 20:15 hrs_23.04.2024 |  | Event-1 : 1235 MW Load Loss in Chhatisgarh at 05:30 hrs_03.04.2024 |  | Event-2: 4870 MW RE Gen Loss and 628 MW Load shedding at 11:24 hrs_06.04.2024 |  | Event-3: 1040 MW Rajasthan RE Gen loss at 10:28 hrs_19.04.2024 |  | Event-4: 1800 MW Gen Loss in APML Tiroda at 20:15 hrs_23.04.2024 |  | Event-1 : 1235 MW Load Loss in Chhatisgarh at 05:30 hrs_03.04.2024 |  | Event-2: 4870 MW RE Gen Loss and 628 MW Load shedding at 11:24 hrs_06.04.2024 |  | Event-3: 1040 MW Rajasthan RE Gen loss at 10:28 hrs_19.04.2024 |  | Event-4: 1800 MW Gen Loss in APML Tiroda at 20:15 hrs_23.04.2024 |  | Event-1 : 1235 MW Load Loss in Chhatisgarh at 05:30 hrs_03.04.2024 |  | Event-2: 4870 MW RE Gen Loss and 628 MW Load shedding at 11:24 hrs_06.04.2024 |  | Event-3: 1040 MW Rajasthan RE Gen loss at 10:28 hrs_19.04.2024 |  | Event-4: 1800 MW Gen Loss in APML Tiroda at 20:15 hrs_23.04.2024 |  | Event-1 : 1235 MW Load Loss in Chhatisgarh at 05:30 hrs_03.04.2024 |  | Event-2: 4870 MW RE Gen Loss and 628 MW Load shedding at 11:24 hrs_06.04.2024 |  | Event-3: 1040 MW Rajasthan RE Gen loss at 10:28 hrs_19.04.2024 |  | Event-4: 1800 MW Gen Loss in APML Tiroda at 20:15 hrs_23.04.2024 |  | Event-1 : 1235 MW Load Loss in Chhatisgarh at 05:30 hrs_03.04.2024 |  | Event-2: 4870 MW RE Gen Loss and 628 MW Load shedding at 11:24 hrs_06.04.2024 |  | Event-3: 1040 MW Rajasthan RE Gen loss at 10:28 hrs_19.04.2024 |  | Event-4: 1800 MW Gen Loss in APML Tiroda at 20:15 hrs_23.04.2024 |  | Event-1 : 1235 MW Load Loss in Chhatisgarh at 05:30 hrs_03.04.2024 |  | Event-2: 4870 MW RE Gen Loss and 628 MW Load shedding at 11:24 hrs_06.04.2024 |  | Event-3: 1040 MW Rajasthan RE Gen loss at 10:28 hrs_19.04.2024 |  | Event-4: 1800 MW Gen Loss in APML Tiroda at 20:15 hrs_23.04.2024 |  | Event-1 : 1235 MW Load Loss in Chhatisgarh at 05:30 hrs_03.04.2024 |  | Event-2: 4870 MW RE Gen Loss and 628 MW Load shedding at 11:24 hrs_06.04.2024 |  | Event-3: 1040 MW Rajasthan RE Gen loss at 10:28 hrs_19.04.2024 |  | Event-4: 1800 MW Gen Loss in APML Tiroda at 20:15 hrs_23.04.2024 |  | Event-1 : 1235 MW Load Loss in Chhatisgarh at 05:30 hrs_03.04.2024 |  | Event-2: 4870 MW RE Gen Loss and 628 MW Load shedding at 11:24 hrs_06.04.2024 |  | Event-3: 1040 MW Rajasthan RE Gen loss at 10:28 hrs_19.04.2024 |  | Event-4: 1800 MW Gen Loss in APML Tiroda at 20:15 hrs_23.04.2024 |  | Event-1 : 1235 MW Load Loss in Chhatisgarh at 05:30 hrs_03.04.2024 |  | Event-2: 4870 MW RE Gen Loss and 628 MW Load shedding at 11:24 hrs_06.04.2024 |  | Event-3: 1040 MW Rajasthan RE Gen loss at 10:28 hrs_19.04.2024 |  | Event-4: 1800 MW Gen Loss in APML Tiroda at 20:15 hrs_23.04.2024
|  |  | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station | RLDC HDR Data (10 sec or better resolution) | High Resolution Data (1 sec or better resolution) submitted by generating station
1 | Actual Net Interchange before the Event, PA (Import +ve / Export -ve) | MW | -1529.084 | DATA NOT RECEIVED | -840.3776 | DATA NOT RECEIVED | -570.5939 | DATA NOT RECEIVED | -715.3503 | DATA NOT RECEIVED | -489.415 | DATA NOT RECEIVED | -469.53 | DATA NOT RECEIVED | -270.1164 | DATA NOT RECEIVED | -463.1267 | DATA NOT RECEIVED | -696.6702 | DATA NOT RECEIVED | -719.4291 | DATA NOT RECEIVED | -437.8174 | DATA NOT RECEIVED | -699.3095 | DATA NOT RECEIVED | -1383.6663 | DATA NOT RECEIVED | -1352.2904 | -1425.059 | -745.4877 | -812.0046 | -1366.2905 | -1453.6026 | -932.5747 | -1001.6 | -913.0871 | -986.5 | -858.1442 | -923 | -913.541 | -982.2 | -632.9081 | DATA NOT RECEIVED | -369.8347 | DATA NOT RECEIVED | -801.0518 | DATA NOT RECEIVED | -1156.3782 | DATA NOT RECEIVED | -640.0016 | DATA NOT RECEIVED | -352.2451 | DATA NOT RECEIVED | -703.9722 | DATA NOT RECEIVED | -1144.5078 | DATA NOT RECEIVED | -659.6753 | -706.2164 | -655.1227 | -707.5723 | -249.4259 | -276.2731 | -656.9012 | -704.8606 | -1013.0449 | -1046.24 | -1009.9344 | -1044.015 | -560.8123 | -583.2007 | -985.6325 | -1018.57 | -240.5359 | -540 | -383.8531 | -416.2513 | -292.5999 | -321.8073 | -488.3445 | -523.2184 | -565.7996 | -591.41 | -514.0993 | -540.3245 | -556.8 | -595.7599 | -560.7001 | -593.1821 | -920.881 | DATA NOT RECEIVED | -893.8925 | DATA NOT RECEIVED | -549.8159 | -609.0072 | -871.4761 | -932.5865 | 31.8675 | DATA NOT RECEIVED | -33.6648 | DATA NOT RECEIVED | -0.068323 | DATA NOT RECEIVED | -31.7984 | DATA NOT RECEIVED | -1941.9666 | -1976.6206 | -1905.7827 | -1948.3691 | -1059.3829 | -1091.2479 | -1829.429 | -1901.886 | -1331.6949 | -1410.141 | -1488.8245 | -1585.855 | -1476.8618 | -1562 | -1494.8347 | -1586.9 | -1286.9712 | -1318 | -1265.198 | -1307 | -1160.5103 | -1199.7546 | -1272.8151 | -1310
2 | Actual Net Interchange after the Event, PB (Import +ve / Export -ve) | MW | -1525.9252 |  | -873.2532 |  | -584.4164 |  | -716.8864 |  | -488.2415 |  | -471.6418 |  | -282.3441 |  | -472.1473 |  | -689.7794 |  | -728.3337 |  | -433.7595 |  | -700.8544 |  | -1387.4874 |  | -1350.0588 | -1420.286 | -783.4293 | -831.9623 | -1374.783 | -1458.4921 | -927.3408 | -1004.8 | -926.7126 | -995.2 | -858.5161 | -919 | -923.2823 | -994.8 | -633.8831 |  | -378.2433 |  | -803.2479 |  | -1155.144 |  | -638.9816 |  | -351.8685 |  | -696.4395 |  | -1155.6552 |  | -658.3494 | -696.4872 | -667.2055 | -715.7315 | -256.5497 | -282.7911 | -657.7063 | -701.4589 | -1013.9672 | -1046.64 | -1011.1668 | -1046.373 | -563.2051 | -583.9662 | -990.8703 | -1023.35 | -240.1265 | -540 | -402.3304 | -434.6518 | -291.8456 | -320.4354 | -488.4892 | -523.2472 | -565.7996 | -591.16 | -514.5992 | -538.5756 | -556.8 | -594.3716 | -559.6 | -592.8348 | -923.7017 |  | -899.6808 |  | -571.6696 | -619.794 | -896.402 | -951.9193 | 31.8675 |  | -33.8031 |  | -0.068323 |  | -31.9366 |  | -1921.7802 | -1962.1837 | -1927.0105 | -1972.1263 | -1076.6514 | -1099.7897 | -1827.1895 | -1902.7812 | -1336.7831 | -1412.514 | -1492.9886 | -1582.616 | -1489.5869 | -1567 | -1500.682 | -1595.4 | -1280.1775 | -1313 | -1272.0258 | -1327 | -1181.1102 | -1217.8938 | -1286.4524 | -1316
3 | Change in net interchange, PB-PA (2 - 1) | MW | 3.1588 |  | -32.8755 |  | -13.8226 |  | -1.5361 |  | 1.1735 |  | -2.1118 |  | -12.2277 |  | -9.0206 |  | 6.8908 |  | -8.9046 |  | 4.0579 |  | -1.5449 |  | -3.8212 |  | 2.2316 | 4.773 | -37.9416 | -19.9577 | -8.4924 | -4.8895 | 5.2339 | -3.2 | -13.6255 | -8.7 | -0.37189 | 4.1 | -9.7413 | -12.6 | -0.97498 |  | -8.4085 |  | -2.196 |  | 1.2341 |  | 1.02 |  | 0.37662 |  | 7.5328 |  | -11.1473 |  | 1.3259 | 9.7292 | -12.0828 | -8.1592 | -7.1238 | -6.518 | -0.80511 | 3.4017 | -0.92224 | -0.4 | -1.2324 | -2.358 | -2.3929 | -0.7655 | -5.2378 | -4.78 | 0.40941 | 0 | -18.4773 | -18.4005 | 0.75439 | 1.3719 | -0.14474 | -0.0288 | 0 | 0.25 | -0.49988 | 1.7489 | 0 | 1.3883 | 1.1001 | 0.3473 | -2.8207 |  | -5.7884 |  | -21.8538 | -10.7868 | -24.9259 | -19.3328 | 0 |  | -0.13825 |  | 0 |  | -0.13825 |  | 20.1864 | 14.4369 | -21.2278 | -23.7572 | -17.2684 | -8.5418 | 2.2395 | -0.8952 | -5.0881 | -2.373 | -4.1642 | 3.239 | -12.7251 | -5 | -5.8473 | -8.5 | 6.7937 | 4.3 | -6.8278 | -20 | -20.6 | -18.1392 | -13.6373 | -6.7
4 | Generation Loss (+) / Load Throw off (-) during the Event, PL | MW | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PLANT OUT | [7 empty] | PLANT OUT
5 | Control Area Response, ΔP=(PB-PA) – PL (3-4) | MW | 3.1588 |  | -32.8755 |  | -13.8226 |  | -1.5361 |  | 1.1735 |  | -2.1118 |  | -12.2277 |  | -9.0206 |  | 6.8908 |  | -8.9046 |  | 4.0579 |  | -1.5449 |  | -3.8212 |  | 2.2316 | 4.773 | -37.9416 | -19.9577 | -8.4924 | -4.8895 | 5.2339 | -3.2 | -13.6255 | -8.7 | -0.37189 | 4.1 | -9.7413 | -12.6 | -0.97498 |  | -8.4085 |  | -2.196 |  | 1.2341 |  | 1.02 |  | 0.37662 |  | 7.5328 |  | -11.1473 |  | 1.3259 | 9.7292 | -12.0828 | -8.1592 | -7.1238 | -6.518 | -0.80511 | 3.4017 | -0.92224 | -0.4 | -1.2324 | -2.358 | -2.3929 | -0.7655 | -5.2378 | -4.78 | 0.40941 | 0 | -18.4773 | -18.4005 | 0.75439 | 1.3719 | -0.14474 | -0.0288 | 0 | 0.25 | -0.49988 | 1.7489 | 0 | 1.3883 | 1.1001 | 0.3473 | -2.8207 |  | -5.7884 |  | -21.8538 | -10.7868 | -24.9259 | -19.3328 | 0 |  | -0.13825 |  | 0 |  | -0.13825 |  | 20.1864 | 14.4369 | -21.2278 | -23.7572 | -17.2684 | -8.5418 | 2.2395 | -0.8952 | -5.0881 | -2.373 | -4.1642 | 3.239 | -12.7251 | -5 | -5.8473 | -8.5 | 6.7937 | 4.3 | -6.8278 | -20 | -20.6 | -18.1392 | -13.6373 | -6.7
6 | Frequency before the Event, fA | HZ | 49.959 |  | 50.033 |  | 50.058 |  | 50.058 |  | 49.959 |  | 50.033 |  | 50.058 |  | 50.058 |  | 49.959 |  | 50.033 |  | 50.058 |  | 50.058 |  | 49.959 |  | 50.033 | 50.033 | 50.058 | 50.058 | 50.058 | 50.058 | 49.959 | 49.959 | 50.033 | 50.033 | 50.059 | 50.059 | 50.058 | 50.058 | 49.959 |  | 50.033 |  | 50.058 |  | 50.058 |  | 49.959 |  | 50.033 |  | 50.058 |  | 50.058 |  | 49.959 | 49.959 | 50.033 | 50.033 | 50.058 | 50.058 | 50.058 | 50.058 | 49.959 | 49.959 | 50.033 | 50.033 | 50.0589 | 50.0589 | 50.058 | 50.058 | 49.959 | 49.959 | 50.033 | 50.033 | 50.058 | 50.058 | 50.058 | 50.058 | 49.959 | 49.959 | 50.033 | 50.033 | 50.058 | 50.058 | 50.058 | 50.058 | 49.959 |  | 50.033 |  | 50.058 | 50.058 | 50.058 | 50.058 | 49.959 |  | 50.033 |  | 50.058 |  | 50.058 |  | 49.959 | 49.959 | 50.033 | 50.033 | 50.058 | 50.058 | 50.058 | 50.058 | 49.959 | 49.959 | 50.033 | 50.033 | 50.058 | 50.058 | 50.058 | 50.058 | 49.959 | 49.959 | 50.033 | 50.033 | 50.058 | 50.0589 | 50.058 | 50.058 | [16 empty] | 49.959 |  | 50.033 |  | 50.058 |  | 50.058 |  | 49.959 |  | 50.033 |  | 50.058 |  | 50.058 |  | 49.959 |  | 50.033 |  | 50.058 |  | 50.058
7 | Frequency after the Event, fB | HZ | 50.024 |  | 49.766 |  | 50.006 |  | 49.974 |  | 50.024 |  | 49.766 |  | 50.006 |  | 49.974 |  | 50.024 |  | 49.766 |  | 50.006 |  | 49.974 |  | 50.024 |  | 49.766 | 49.766 | 50.006 | 50.006 | 49.974 | 49.974 | 50.024 | 50.024 | 49.766 | 49.766 | 50.007 | 50.007 | 49.974 | 49.974 | 50.024 |  | 49.766 |  | 50.006 |  | 49.974 |  | 50.024 |  | 49.766 |  | 50.006 |  | 49.974 |  | 50.024 | 50.024 | 49.766 | 49.766 | 50.006 | 50.006 | 49.974 | 49.974 | 50.024 | 50.024 | 49.766 | 49.766 | 50.0069 | 50.0069 | 49.974 | 49.974 | 50.024 | 50.024 | 49.766 | 49.766 | 50.006 | 50.006 | 49.974 | 49.974 | 50.024 | 50.024 | 49.766 | 49.766 | 50.006 | 50.006 | 49.974 | 49.974 | 50.024 |  | 49.766 |  | 50.006 | 50.006 | 49.974 | 49.974 | 50.024 |  | 49.766 |  | 50.006 |  | 49.974 |  | 50.024 | 50.024 | 49.766 | 49.766 | 50.006 | 50.006 | 49.974 | 49.974 | 50.024 | 50.024 | 49.766 | 49.766 | 50.006 | 50.006 | 49.974 | 49.974 | 50.024 | 50.024 | 49.766 | 49.766 | 50.006 | 50.0069 | 49.974 | 49.974 | [16 empty] | 50.024 |  | 49.766 |  | 50.006 |  | 49.974 |  | 50.024 |  | 49.766 |  | 50.006 |  | 49.974 |  | 50.024 |  | 49.766 |  | 50.006 |  | 49.974
8 | Change in Frequency, Δf=(fB-fA) (7-6) | HZ | 0.065 |  | -0.267 |  | -0.052 |  | -0.084 |  | 0.065 |  | -0.267 |  | -0.052 |  | -0.084 |  | 0.065 |  | -0.267 |  | -0.052 |  | -0.084 |  | 0.065 |  | -0.267 | -0.267 | -0.052 | -0.052 | -0.084 | -0.084 | 0.065 | 0.065 | -0.267 | -0.267 | -0.052 | -0.05 | -0.084 | -0.084 | 0.065 |  | -0.267 |  | -0.052 |  | -0.084 |  | 0.065 |  | -0.267 |  | -0.052 |  | -0.084 |  | 0.065 | 0.065 | -0.267 | -0.267 | -0.052 | -0.052 | -0.084 | -0.084 | 0.065 | 0.065 | -0.267 | -0.267 | -0.052 | -0.052 | -0.084 | -0.084 | 0.065 | 0.065 | -0.267 | -0.267 | -0.052 | -0.052 | -0.084 | -0.084 | 0.065 | 0.065 | -0.267 | -0.267 | -0.052 | -0.052 | -0.084 | -0.084 | 0.065 |  | -0.267 |  | -0.052 | -0.052 | -0.084 | -0.084 | 0.065 |  | -0.267 |  | -0.052 |  | -0.084 |  | 0.065 | 0.065 | -0.267 | -0.267 | -0.052 | -0.052 | -0.084 | -0.084 | 0.065 | 0.065 | -0.267 | -0.267 | -0.052 | -0.052 | -0.084 | -0.084 | 0.065 | 0.06 | -0.267 | -0.27 | -0.052 | -0.052 | -0.084 | -0.08 | [16 empty] | 0.065 |  | -0.267 |  | -0.052 |  | -0.084 |  | 0.065 |  | -0.267 |  | -0.052 |  | -0.084 |  | 0.065 |  | -0.267 |  | -0.052 |  | -0.084
9 | Frequency Response Characteristic, ΔP/ Δf (5 / 8) | MW/Hz | 48.5971 |  | 123.1294 |  | 265.8187 |  | 18.2866 |  | 18.0537 |  | 7.9094 |  | 235.1485 |  | 107.3877 |  | 106.0124 |  | 33.3506 |  | -78.0364 |  | 18.3919 |  | -58.7872 |  | -8.3579 | -17.8764 | 729.6459 | 383.8019 | 101.1004 | 58.2083 | 80.5223 | -49.2308 | 51.032 | 32.5843 | 7.1517 | -79 | 115.9683 | 150 | -14.9996 |  | 31.4925 |  | 42.2316 |  | -14.692 |  | 15.6926 |  | -1.4106 |  | -144.8611 |  | 132.7064 |  | 20.3979 | 149.68 | 45.2538 | 30.5588 | 136.9963 | 125.3462 | 9.5847 | -40.4964 | -14.1883 | -6.1538 | 4.6156 | 8.8315 | 46.017 | 14.7212 | 62.3547 | 56.9048 | 6.2986 | 0 | 69.2032 | 68.9157 | -14.5076 | -26.3827 | 1.7232 | 0.34286 | 0 | 3.8462 | 1.8722 | -6.5502 | 0 | -26.6981 | -13.0964 | -4.1345 | -43.396 |  | 21.6794 |  | 420.2646 | 207.4385 | 296.7369 | 230.1524 | 0 |  | 0.5178 |  | 0 |  | 1.6459 |  | 310.56 | 222.1062 | 79.5048 | 88.9783 | 332.0852 | 164.2654 | -26.6607 | 10.6571 | -78.279 | -36.5077 | 15.5962 | -12.1311 | 244.7134 | 96.1538 | 69.6106 | 101.1905 | 104.5185 | 66 | 25.5721 | 75 | 396.1534 | 348.8308 | 162.3492 | 80
10 | Frequency Response Obligation (FRO) of each control area | MW/Hz | 45.3666 |  | 70.5703 |  | 70.5703 |  | 45.3666 |  | 16.8745 |  | 26.2492 |  | 26.2492 |  | 16.8745 |  | 22.7614 |  | 35.4067 |  | 35.4067 |  | 22.7614 |  | 46.6975 |  | 72.6405 | 72.6405 | 72.6405 | 72.6405 | 46.6975 | 46.6975 | 34.9649 | 34.9649 | 54.3898 | 54.3898 | 54.3898 | 54 | 34.9649 | 34.9649 | 27.5288 |  | 42.8225 |  | 42.8225 |  | 27.5288 |  | 37.4087 |  | 58.1913 |  | 58.1913 |  | 37.4087 |  | 24.1363 | 24.1363 | 37.5454 | 37.5454 | 37.5454 | 37.5454 | 24.1363 | 24.1363 | 34.1865 | 34.1865 | 53.179 | 53.179 | 53.179 | 53.179 | 34.1865 | 34.1865 | 15.6721 | 15.6721 | 24.3789 | 24.3789 | 24.3789 | 24.3789 | 15.6721 | 15.6721 | 38.2973 | 38.2973 | 59.5735 | 59.5735 | 59.5735 | 59.5735 | 38.2973 | 38.2973 | 29.8224 |  | 46.3904 |  | 46.3904 | 46.3904 | 29.8224 | 29.8224 | 2.6932 |  | 4.1895 |  | 4.1895 |  | 2.6932 |  | 67.9155 | 67.9155 | 105.6464 | 105.6464 | 105.6464 | 105.6464 | 67.9155 | 67.9155 | 53.5476 | 53.5476 | 83.2963 | 83.2963 | 83.2963 | 83.2963 | 53.5476 | 53.5476 | 24.3359 | 24 | 37.8559 | 38 | 37.8559 | 37.8559 | 24.3359 | 24
11 | Frequency Response Performance (FRP) (9/10) |  | 1.0712 |  | 1.7448 |  | 3.7667 |  | 0.40308 |  | 1.0699 |  | 0.30132 |  | 8.9583 |  | 6.3639 |  | 4.6575 |  | 0.94193 |  | -2.204 |  | 0.80803 |  | -1.2589 |  | -0.11506 | -0.24609 | 10.0446 | 5.2836 | 2.165 | 1.2465 | 2.3029 | -1.408 | 0.93827 | 0.59909 | 0.13149 | -1.45 | 3.3167 | 4.29 | -0.54487 |  | 0.73542 |  | 0.9862 |  | -0.5337 |  | 0.41949 |  | -0.02424 |  | -2.4894 |  | 3.5475 |  | 0.84512 | 6.2014 | 1.2053 | 0.81392 | 3.6488 | 3.3385 | 0.39711 | -1.6778 | -0.41503 | -0.18001 | 0.086793 | 0.16607 | 0.86532 | 0.27682 | 1.824 | 1.6645 | 0.4019 | 0 | 2.8387 | 2.8269 | -0.59509 | -1.0822 | 0.10995 | 0.021877 | 0 | 0.10043 | 0.031427 | -0.10995 | 0 | -0.44815 | -0.34197 | -0.10796 | -1.4551 |  | 0.46732 |  | 9.0593 | 4.4716 | 9.9501 | 7.7174 | 0 |  | 0.1236 |  | 0 |  | 0.61112 |  | 4.5727 | 3.2703 | 0.75256 | 0.84223 | 3.1434 | 1.5549 | -0.39256 | 0.15692 | -1.4619 | -0.68178 | 0.18724 | -0.14564 | 2.9379 | 1.1544 | 1.3 | 1.8897 | 4.2948 | 2.73 | 0.67551 | 1.97 | 10.4648 | 9.2147 | 6.6712 | 3.3
Consideration of FRP for computation of Average Monthly FRP, Beta ‘ß’ |  |  | 1 | 0 | 1 | 0 | 1 | 0 | 0.4 | 0 | 1 | 0 | 0.3 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0.94 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0.93 | 0.59 | 0.13 | 0 | 1 | 1 | 0 | 0 | 0.73 | 0 | 0.98 | 0 | 0 | 0 | 0.41 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.84 | 1 | 1 | 0.81 | 1 | 1 | 0.39 | 0 | 0 | 0 | 0.08 | 0.16 | 0.86 | 0.27 | 1 | 1 | 0.4 | 0 | 1 | 1 | 0 | 0 | 0.1 | 0.02 | 0 | 0.1 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0.12 | 0 | 0 | 0 | 0.61 | 0 | 1 | 1 | 0.75 | 0.84 | 1 | 1 | 0 | 0.15 | 0 | 0 | 0.18 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0.67 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Average Monthly Frequency Response Performance, Beta ‘ß’ for April, 2024 | [8 empty] | 0.85 | DATA N/R | [6 empty] | 0.825 | DATA N/R | [6 empty] | 0.685 | DATA N/R | [14 empty] | 0.765 | 0.3975 | [6 empty] | 0.4275 | DATA N/R | [6 empty] | 0.3525 | DATA N/R | [6 empty] | 0.8075 | 0.7025 | [6 empty] | 0.485 | 0.3575 |  | GEN data freeze |  |  |  |  | 0.375 | 0.34 | [6 empty] | 0.0075 | 0.025 | [6 empty] | 0.615 | 1 | DATA FREEZE |  |  |  | No gen |  | 0.365 | 0.365 | [5 empty] | -1 | 0.6875 | 0.7475 | [6 empty] | 0.545 | 0.5
[9 empty] | 0.85 | 0.85 | [6 empty] | 0.825 | 0.825 | [6 empty] | 0.685 | 0.685 | [6 empty] | 0.5 | 0.5 | [6 empty] | 0.765 | 0.3975 | [6 empty] | 0.4275 | 0.4275 | [6 empty] | 0.3525 | 0.3525 | [6 empty] | 0.8075 | 0.7025 | [6 empty] | 0.485 | 0.3575 | [6 empty] | 0.375 | 0.355 | [6 empty] | 0.0075 | 0.025 | [6 empty] | 0.615 | 0.615 | [14 empty] | 0.6875 | 0.7475 | [6 empty] | 0.545 | 0.5 | [6 empty] | 0.9175 | 1
[9 empty] | SCADA FRP | GEN FRP | [6 empty] | SCADA FRP | GEN FRP | [6 empty] | SCADA FRP | GEN FRP | [6 empty] | SCADA FRP | GEN FRP | [6 empty] | SCADA FRP | GEN FRP | [14 empty] | SCADA FRP | GEN FRP | [6 empty] | SCADA FRP | GEN FRP | [14 empty] | SCADA FRP | GEN FRP | [6 empty] | SCADA FRP | GEN FRP | [6 empty] | SCADA FRP | GEN FRP | [6 empty] | SCADA FRP | GEN FRP | [6 empty] | SCADA FRP | GEN FRP | [14 empty] | SCADA FRP | GEN FRP
| Average Monthly Frequency Response Performance, Beta ‘ß’ for April, 2024 | [8 empty] | 0.85 | [7 empty] | 0.82 | [7 empty] | 0.68 | [7 empty] | 0.5 | [7 empty] | 0.39 | [7 empty] | 0.42 | [7 empty] | 0.35 | [7 empty] | 0.7 | [7 empty] | 0.35 | [7 empty] | 0.35 | [7 empty] | 0.02 | [7 empty] | 0.61 | [15 empty] | 0.74 | [7 empty] | 0.5 | [7 empty] | 1
| Considerations for Beta Calculation | [70 empty] | -1
| IN CASE OF NON RECEIPT OF DATA, ERLDC SCADA DATA HAS BEEN USED TO CALCULATED AVERAGE BETA | [60 empty] | -1
IN CASE OF PLANT OUTAGE DURING ANY EVENT, THAT EVENT WILL BE EXCLUDED FROM BETA CALCULATION
| IN CASE OF PLANT DATA FREEZE DURING ANY EVENT, ERLDC SCADA WLL BE USED FOR BETA CALCULATION | [66 empty] | -1 | [11 empty] | -1
| THE FRP VALUE & BETA WILL BE TRUNCATED TO 2 DECIMAL POINTS | [110 empty] | -1
If FRP for an event is less than or equal to 0, FRP (Event i) shall be equal to 0.
| If FRP for an event lies between 0 to 1, FRP (Event i) shall be equal to the calculated value. | [86 empty] | -1
If FRP for an event is greater than or equal to 1, FRP (Event i) shall be equal to 1.
-1