## 220 KV
ERPC::KOLKATA
DETAILS OF PROTECTION AUDIT
A) | General Imformation :
1) | Name of Sub-station |  |  | 400/220kV Subhasgram Substation |  |  | 2) | Date of commissioning 2007 |  | 3) | Type of Bus Switching Scheme: |  | DMT | Whether SLD collected of Not: |  | 5) | Name of Audit Team
6) | Instrument transformer
A | Current transformer (CT)
1 | Location of CT |  |  | 204 Bay (BC) |  |  | (Please fill-up for each CT)
a | Date of Testing |  |  | 2007
b | CT ratio Test
|  |  | Phase Identification |  | Make/Model |  | Core I |  | Core II |  | Core III |  | Core IV |  | Core V |  | Core VI
1 | Ratio Adopted | [5 empty] | Bus Bar-I Prot |  | Bus Bar-II Prot |  | Metering |  | LBB |  | Spare
[7 empty] | 1600/1 |  | 1600/1 |  | 1600/1 |  | 1600/1 |  | 1600/1
2 | Ratio measured |  | R |  | CGL |  | 1602 |  | 1600.6 |  | 1600.7 |  | 1601.6
|  |  | Y |  | CGL |  | 1601 |  | 1599.2 |  | 1599.7 |  | 1600.4
|  |  | B |  | CGL |  | 1601.5 |  | 1601.3 |  | 1598.9 |  | 1601.1
3 | Error calculated |  | R |  | CGL |  | -0.00125 |  | -0.00037486 |  | -0.0004375 |  | -0.001
|  |  | Y |  | CGL |  | -0.000625 |  | 0.0005 |  | 0.0001875 |  | -0.00025
|  |  | B |  | CGL |  | -0.0009375 |  | -0.0008125 |  | 0.0006875 |  | -0.0006875
1 | Location of CT |  |  | 205 KLC Line Bay |  |  | (Please fill-up for each CT)
a | Date of Testing |  |  | 2007
b | CT ratio Test
|  |  | Phase Identification |  | Make/Model |  | Core I |  | Core II |  | Core III |  | Core IV |  | Core V |  | Core VI
1 | Ratio Adopted | [5 empty] | Spare |  | Bus bar protection |  | Metering |  | Main – II & LBB |  | Main I
[7 empty] | 1600/1 |  | 1600/1 |  | 1600/1 |  | 800/1 |  | 800/1
2 | Ratio measured |  | R |  | CGL |  |  |  | 1601 |  | 1600.2 |  | 800.6 |  | 801.2
|  |  | Y |  | CGL |  |  |  | 1601.4 |  | 1600.8 |  | 801.2 |  | 800.9
|  |  | B |  | CGL |  |  |  | 1600.3 |  | 1599.3 |  | 800.5 |  | 799.7
3 | Error calculated |  | R |  | CGL |  |  |  | -0.000625 |  | -0.000125 |  | -0.00075 |  | -0.0014978
|  |  | Y |  | CGL |  |  |  | -0.000875 |  | -0.00049975 |  | -0.0015 |  | -0.001125
|  |  | B |  | CGL |  |  |  | -0.0001875 |  | 0.0004375 |  | -0.00062461 |  | 0.000375
1 | Location of CT |  |  | 206 New Town Line Bay |  |  | (Please fill-up for each CT)
a | Date of Testing |  |  | 2007
b | CT ratio Test
|  |  | Phase Identification |  | Make/Model |  | Core I |  | Core II |  | Core III |  | Core IV |  | Core V |  | Core VI
1 | Ratio Adopted | [5 empty] | Spare |  | Bus bar protection |  | Metering |  | Main -II & LBB |  | Main I
[7 empty] | 1600/1 |  | 1600/1 |  | 1600/1 |  | 800/1 |  | 800/1
2 | Ratio measured |  | R |  | CGL |  |  |  | 1600.2 |  | 1601.2 |  | 800.3 |  | 801.7
|  |  | Y |  | CGL |  |  |  | 1599.5 |  | 1600.7 |  | 799.7 |  | 799.9
|  |  | B |  | CGL |  |  |  | 1598.9 |  | 1599.8 |  | 801.5 |  | 800.7
3 | Error calculated |  | R |  | CGL |  |  |  | -0.000125 |  | -0.00075 |  | -0.00037486 |  | -0.002125
|  |  | Y |  | CGL |  |  |  | 0.0003126 |  | -0.0004375 |  | 0.000375 |  | 0.000125
|  |  | B |  | CGL |  |  |  | 0.0006875 |  | 0.000125 |  | -0.001875 |  | -0.000875
1 | Location of CT |  |  | 207 Subhasgram Subhasgram Line 1 Bay |  |  | (Please fill-up for each CT)
a | Date of Testing |  |  | 2007
b | CT ratio Test
|  |  | Phase Identification |  | Make/Model |  | Core I |  | Core II |  | Core III |  | Core IV |  | Core V |  | Core VI
1 | Ratio Adopted | [5 empty] | Spare |  | Bus bar protection |  | Metering |  | Main-II & LBB |  | Main I
[7 empty] | 1600/1 |  | 1600/1 |  | 1600/1 |  | 1600/1 |  | 1600/1
2 | Ratio measured |  | R |  | CGL |  |  |  | 1601.5 |  | 1599.8 |  | 1601.4 |  | 1599.5
|  |  | Y |  | CGL |  |  |  | 1601.3 |  | 1600.3 |  | 1600.1 |  | 1601.2
|  |  | B |  | CGL |  |  |  | 1600.4 |  | 1599.3 |  | 1601.7 |  | 1600.9
3 | Error calculated |  | R |  | CGL |  |  |  | -0.0009375 |  | 0.000125 |  | -0.000875 |  | 0.0003125
|  |  | Y |  | CGL |  |  |  | -0.0008125 |  | -0.0001875 |  | -6.25e-05 |  | -0.00075
|  |  | B |  | CGL |  |  |  | -0.00025 |  | 0.0004375 |  | -0.0010625 |  | -0.0005625
1 | Location of CT |  |  | 208 ICT 1 Bay |  |  | (Please fill-up for each CT)
a | Date of Testing |  |  | 2007
b | CT ratio Test
|  |  | Phase Identification |  | Make/Model |  | Core I |  | Core II |  | Core III |  | Core IV |  | Core V |  | Core VI
1 | Ratio Adopted | [5 empty] | Spare |  | Bus bar protection |  | SPARE |  | Backup protection & LBB protection |  | Differential Protection
[7 empty] | 1600/1 |  | 1600/1 |  | 800/1 |  | 800/1 |  | 800/1
2 | Ratio measured |  | R |  | CGL |  |  |  | 1601.5 |  |  |  | 798.7 |  | 801.2
|  |  | Y |  | CGL |  |  |  | 1600.2 |  |  |  | 799.8 |  | 800.3
|  |  | B |  | CGL |  |  |  | 1599.8 |  |  |  | 800.6 |  | 799.7
3 | Error calculated |  | R |  | CGL |  |  |  | -0.0009375 |  |  |  | 0.0016276 |  | -0.0015
|  |  | Y |  | CGL
|  |  | Y |  | CGL |  |  |  | -0.000125 |  |  |  | 0.00025 |  | -0.00037486
|  |  | B |  | CGL |  |  |  | 0.000125 |  |  |  | -0.00075 |  | 0.000375
1 | Location of CT |  |  | 209 Subhasgram Subhasgram Line 2 Bay |  |  | (Please fill-up for each CT)
a | Date of Testing |  |  | 2007
b | CT ratio Test
|  |  | Phase Identification |  | Make/Model |  | Core I |  | Core II |  | Core III |  | Core IV |  | Core V |  | Core VI
1 | Ratio Adopted | [5 empty] | Spare |  | Bus bar protection |  | Metering |  | Main -II & LBB |  | Main I
[7 empty] | 1600/1 |  | 1600/1 |  | 1600/1 |  | 1600/1 |  | 1600/1
2 | Ratio measured |  | R |  | CGL |  |  |  | 1599.5 |  | 1601.4 |  | 1602 |  | 1602.2
|  |  | Y |  | CGL |  |  |  | 1601.3 |  | 1600.9 |  | 1600.6 |  | 1601.5
|  |  | B |  | CGL |  |  |  | 1600.4 |  | 1598.7 |  | 1599.4 |  | 1600.3
3 | Error calculated |  | R |  | CGL |  |  |  | 0.0003125 |  | -0.000875 |  | -0.00125 |  | -0.001375
|  |  | Y |  | CGL |  |  |  | -0.0008125 |  | -0.0005625 |  | -0.000375 |  | -0.0009375
|  |  | B |  | CGL |  |  |  | -0.00025 |  | 0.0008125 |  | 0.000375 |  | -0.0001875
1 | Location of CT |  |  | 210 ICT 2 Bay |  |  | (Please fill-up for each CT)
a | Date of Testing |  |  | 2007
b | CT ratio Test
|  |  | Phase Identification |  | Make/Model |  | Core I |  | Core II |  | Core III |  | Core IV |  | Core V |  | Core VI
1 | Ratio Adopted | [5 empty] | Spare |  | Bus bar prot |  | Spare |  | Backup protection & LBB protection |  | Diff Prot
[7 empty] | 1600/1 |  | 1600/1 |  | 1600/1 |  | 800/1 |  | 800/1
2 | Ratio measured |  | R |  | CGL |  |  |  | 1602.3 |  |  |  | 802.4 |  | 801.9
|  |  | Y |  | CGL |  |  |  | 1598.5 |  |  |  | 801.6 |  | 800.3
|  |  | B |  | CGL |  |  |  | 1600.2 |  |  |  | 800.9 |  | 799.7
3 | Error calculated |  | R |  | CGL |  |  |  | -0.0014375 |  |  |  | -0.003 |  | -0.002375
|  |  | Y |  | CGL |  |  |  | 0.0009375 |  |  |  | -0.002 |  | -0.000375
|  |  | B |  | CGL |  |  |  | -0.000125 |  |  |  | -0.001125 |  | 0.000375
1 | Location of CT |  |  | 212 TBC Bay |  |  | (Please fill-up for each CT)
a | Date of Testing |  |  | 2007
b | CT ratio Test
|  |  | Phase Identification |  | Make/Model |  | Core I |  | Core II |  | Core III |  | Core IV |  | Core V |  | Core VI
1 | Ratio Adopted | [5 empty] | Bus bar prot |  | Bus bar prot |  | Metering |  | LBB Protection |  | Spare
[7 empty] | 1600/1 |  | 1600/1 |  | 800/1 |  | 800/1 |  | 1600/1
2 | Ratio measured |  | R |  | CGL |  | 1600.7 |  | 1600.8 |  | 801.2 |  | 802.3
|  |  | Y |  | CGL |  | 1602.2 |  | 1601.9 |  | 802.2 |  | 801.7
|  |  | B |  | CGL |  | 1601.6 |  | 1601.7 |  | 801.7 |  | 799.8
3 | Error calculated |  | R |  | CGL |  | -0.0004375 |  | -0.0005 |  | -0.0015 |  | -0.0028668
|  |  | Y |  | CGL |  | -0.001375 |  | -0.0011875 |  | -0.00275 |  | -0.002125
|  |  | B |  | CGL |  | -0.001 |  | -0.0010625 |  | -0.002125 |  | 0.00025
1 | Location of CT |  |  | 215 Future Line 1 Bay |  |  | (Please fill-up for each CT)
a | Date of Testing |  |  | 2007
b | CT ratio Test
|  |  | Phase Identification |  | Make/Model |  | Core I |  | Core II |  | Core III |  | Core IV |  | Core V |  | Core VI
1 | Ratio Adopted | [5 empty] | Spare |  | Bus bar protec |  | Metering |  | Main -II & LBB |  | Main I
[7 empty] | 1600/1 |  | 1600/1 |  | 1600/1 |  | 800/1 |  | 800/1
2 | Ratio measured |  | R |  | Siemens |  |  |  | 1601.5 |  | 1600.7 |  | 800.5 |  | 801.4
|  |  | Y |  | Siemens |  |  |  | 1599.8 |  | 1599.6 |  | 800.2 |  | 799.8
|  |  | B |  | Siemens |  |  |  | 1602.1 |  | 1601.8 |  | 801.8 |  | 802.4
3 | Error calculated |  | R |  | Siemens |  |  |  | -0.0009375 |  | -0.0004375 |  | -0.000625 |  | -0.00175
|  |  | Y |  | Siemens |  |  |  | 0.000125 |  | 0.00025 |  | -0.00025 |  | 0.00025
|  |  | B |  | Siemens |  |  |  | -0.0013125 |  | -0.001125 |  | -0.00225 |  | -0.003
1 | Location of CT |  |  | 216 Future Line 2 Bay |  |  | (Please fill-up for each CT)
a | Date of Testing |  |  | 2007
b | CT ratio Test
|  |  | Phase Identification |  | Make/Model |  | Core I |  | Core II |  | Core III |  | Core IV |  | Core V |  | Core VI
1 | Ratio Adopted | [5 empty] | Spare |  | Bus bar prot |  | Metering |  | Main -II & LBB |  | Main I
[7 empty] | 1600/1 |  | 1600/1 |  | 1600/1 |  | 800/1 |  | 800/1
2 | Ratio measured |  | R |  | Siemens |  |  |  | 1600.6 |  | 1599.3 |  | 800.6 |  | 800.9
|  |  | Y |  | Siemens |  |  |  | 1601.7 |  | 1598.3 |  | 798.8 |  | 799.4
|  |  | B |  | Siemens |  |  |  | 1602.3 |  | 1601.8 |  | 801.4 |  | 801.7
3 | Error calculated |  | R |  | Siemens |  |  |  | -0.000375 |  | 0.0004375 |  | -0.00075 |  | -0.001125
|  |  | Y |  | Siemens |  |  |  | -0.0010625 |  | 0.0010625 |  | 0.0015 |  | 0.00075
|  |  | B |  | Siemens |  |  |  | -0.0014375 |  | -0.001125 |  | -0.00175 |  | -0.002125
1 | Location of CT |  |  | 201 ICT 5 Bay |  |  | (Please fill-up for each CT)
a | Date of Testing |  |  | 2015
b | CT ratio Test
|  |  | Phase Identification |  | Make/Model |  | Core I |  | Core II |  | Core III |  | Core IV |  | Core V |  | Core VI
1 | Ratio Adopted | [5 empty] | Spare |  | Bus bar prot |  | SPARE |  | Backup protection & LBB protection |  | Diff Prot
[7 empty] | 1600/1 |  | 1600/1 |  | 1600/1 |  | 800/1 |  | 800/1
2 | Ratio measured |  | R |  | Siemens |  |  |  | 1598.2 |  |  |  | 800.2 |  | 799.4
|  |  | Y |  | Siemens |  |  |  | 1600.3 |  |  |  | 799.6 |  | 800.5
|  |  | B |  | Siemens |  |  |  | 1601.7 |  |  |  | 802.2 |  | 801.6
3 | Error calculated |  | R |  | Siemens |  |  |  | 0.001125 |  |  |  | -0.00025 |  | 0.00075
|  |  | Y |  | Siemens |  |  |  | -0.0001875 |  |  |  | 0.0005 |  | -0.000625
|  |  | B |  | Siemens |  |  |  | -0.0010625 |  |  |  | -0.00275 |  | -0.002
1 | Location of CVT |  |  | 220 KV Subhasgram -Subhasgram Line-1 |  |  | (Please fill-up for each CVT)
a | Date of Testing |  |  | 2007
b | CVT ratio Test
|  |  | Phase Identification |  | Make/Model |  | Core I |  | Core II |  | Core III
1 | Ratio Adopted | [5 empty] | PROTECTION |  | PROTECTION |  | METERING
[7 empty] | 2000 |  | 2000 |  | 2000
2 | Ratio measured |  | R |  | CGL |  | 2002 |  | 2002.5 |  | 2001.6
|  |  | Y |  | CGL |  | 2002.3 |  | 2002.4 |  | 2001.8
|  |  | B |  | CGL |  | 2001.9 |  | 2001.5 |  | 2001.6
3 | Error calculated |  | R |  | CGL |  | -0.001 |  | -0.00125 |  | -0.0008
|  |  | Y |  | CGL |  | -0.00115 |  | -0.0012 |  | -0.0009
|  |  | B |  | CGL |  | -0.00095 |  | -0.00075 |  | -0.0008
1 | Location of CVT |  |  | 220 KV Subhasgram -Subhasgram Line-2 |  |  | (Please fill-up for each CVT)
a | Date of Testing |  |  | 2007
b | CVT ratio Test
|  |  | Phase Identification |  | Make/Model |  | Core I |  | Core II |  | Core III
1 | Ratio Adopted | [5 empty] | PROTECTION |  | PROTECTION |  | METERING
[7 empty] | 2000 |  | 2000 |  | 2000
2 | Ratio measured |  | R |  | CGL |  | 2002.5 |  | 2001.9 |  | 2002.3
|  |  | Y |  | CGL |  | 2001.8 |  | 2002.4 |  | 2001.1
|  |  | B |  | CGL |  | 2001.7 |  | 2000.8 |  | 2000.5
3 | Error calculated |  | R |  | CGL |  | -0.00125 |  | -0.00095 |  | -0.00115
|  |  | Y |  | CGL |  | -0.0009 |  | -0.0012 |  | -0.00055
|  |  | B |  | CGL |  | -0.00085 |  | -0.0004 |  | -0.00025
1 | Location of CVT |  |  | 220 KV Subhasgram -KLC Bantala Line |  |  | (Please fill-up for each CVT)
a | Date of Testing |  |  | 2007
b | CVT ratio Test
|  |  | Phase Identification |  | Make/Model |  | Core I |  | Core II |  | Core III
1 | Ratio Adopted | [5 empty] | PROTECTION |  | PROTECTION |  | METERING
[7 empty] | 2000 |  | 2000 |  | 2000
2 | Ratio measured |  | R |  | CGL |  | 2002.7 |  | 2002.6 |  | 2001.6
|  |  | Y |  | CGL |  | 2001.6 |  | 2001.9 |  | 2000.7
|  |  | B |  | CGL |  | 2002.3 |  | 2002.8 |  | 2001.7
3 | Error calculated |  | R |  | CGL |  | -0.00135 |  | -0.0013 |  | -0.0008
|  |  | Y |  | CGL |  | -0.0008 |  | -0.00095 |  | -0.00035
|  |  | B |  | CGL |  | -0.00115 |  | -0.0014 |  | -0.00085
1 | Location of CVT |  |  | 220 KV Subhasgram -Newtown Line |  |  | (Please fill-up for each CVT)
a | Date of Testing |  |  | 2007
b | CVT ratio Test
|  |  | Phase Identification |  | Make/Model |  | Core I |  | Core II |  | Core III
1 | Ratio Adopted | [5 empty] | PROTECTION |  | PROTECTION |  | METERING
[7 empty] | 2000 |  | 2000 |  | 2000
2 | Ratio measured |  | R |  | CGL |  | 2000.9 |  | 2001.3 |  | 2001.1
|  |  | Y |  | CGL |  | 2002.2 |  | 2001.7 |  | 2000.9
|  |  | B |  | CGL |  | 2001.4 |  | 2002.1 |  | 2001.2
3 | Error calculated |  | R |  | CGL |  | -0.00045 |  | -0.00065 |  | -0.00055
|  |  | Y |  | CGL |  | -0.0011 |  | -0.00085 |  | -0.00045
|  |  | B |  | CGL |  | -0.0007 |  | -0.00105 |  | -0.0006
1 | Location of CVT |  |  | 220 KV Future Line Bay 215 |  |  | (Please fill-up for each CVT)
a | Date of Testing |  |  | 2007
b | CVT ratio Test
|  |  | Phase Identification |  | Make/Model |  | Core I |  | Core II |  | Core III
1 | Ratio Adopted | [5 empty] | PROTECTION |  | PROTECTION |  | METERING
[7 empty] | 2000 |  | 2000 |  | 2000
2 | Ratio measured |  | R |  | Siemens |  | 1999.1 |  | 2000.2 |  | 1999.7
|  |  | Y |  | Siemens |  | 2001.5 |  | 2000.9 |  | 2000.3
|  |  | B |  | Siemens |  | 2002.5 |  | 2001.7 |  | 2001.7
3 | Error calculated |  | R |  | Siemens |  | 0.00045 |  | -0.0001 |  | 0.00015
|  |  | Y |  | Siemens |  | -0.00075 |  | -0.00045 |  | -0.00015
|  |  | B |  | Siemens |  | -0.00125 |  | -0.00085 |  | -0.00085
1 | Location of CVT |  |  | 220 KV Future Line Bay 216 |  |  | (Please fill-up for each CVT)
a | Date of Testing |  |  | 2007
b | CVT ratio Test
|  |  | Phase Identification |  | Make/Model |  | Core I |  | Core II |  | Core III
1 | Ratio Adopted | [5 empty] | PROTECTION |  | PROTECTION |  | METERING
[7 empty] | 2000 |  | 2000 |  | 2000
2 | Ratio measured |  | R |  | Siemens |  | 2001.8 |  | 2002.4 |  | 2001.7
|  |  | Y |  | Siemens |  | 1999.2 |  | 2000.5 |  | 1999.7
|  |  | B |  | Siemens |  | 2001.6 |  | 2000.7 |  | 2000.4
3 | Error calculated |  | R |  | Siemens |  | -0.0009 |  | -0.0012 |  | -0.00085
|  |  | Y |  | Siemens |  | 0.0004 |  | -0.00025 |  | 0.00015
|  |  | B |  | Siemens |  | -0.0008 |  | -0.00035 |  | -0.0002
Availability of Protection System
8) | Bus Bar relay (upto 220KV)
1) | Make and Model of Bus Bar relay |  |  | AREVA FAC34
2) | Whethr stability Checks done or not |  |  |  | Yes
3) | Date of Testing |  |  |  | 2007
4) | Remarks (if any) |  |  |  | --
9) | Sub-station protection and monitorining Equipments
Sl. No. | System |  | LBB |  | Avialibility |  | Date of testing | Event Logger |  | Avialibility |  | Synchronising |  | Synchro Check | Setting of
|  |  | (Make & Model) |  | (In service or not) |  |  | (Make & Model) |  | (In service or not) |  | Facility Available or not |  | Relay (Make & Model) | Synchro Check Reley
1) | 220kV System |  | AREVA, MCTI 40 |  | Yes |  | 2011 | AREVA, C-264 |  | Yes |  | Yes |  | AREVA SKD 11 | ϕ= ± 35˚, V= 90%, t= 2 Sec
10) | Transmission Line Protection
SL. No. | Name of the Line |  | Main-I Protection |  | Avialibility |  | Date of testing | Main-II Protection |  | Avialibility |  | Date of testing | LBB Protection | Avialibility | Date of testing
|  |  | (Make & Model) |  | (In service or not) |  |  | (Make & Model) |  | (In service or not) |  |  | (Make & Model) | (In service or not)
1) | 220kV Subhasgram- Subhasgram Line-1 |  | AREVA, MICOM-P 442 |  | YES |  | 2015 | Siemens, SIPROTEC- 7SA52 |  | Yes |  | 2015 | AREVA, MCTI | YES | 2011
| Name of the Line |  | PLCC/Protection Coupler |  | Avialibility |  | Date of testing | Disturbance recorder (DR) |  | Time Synchr.Unit |  | Date of testing | Any Other
|  |  | (Make & Model) |  | (In service or not) |  |  | (Make & Model) |  | (Make & Model) |  |  | Protection
1) | 220kV Subhasgram- Subhasgram Line-1 |  | Owned by WBSETCL |  | Yes |  |  | In built in Main I |  | Arbitor, 1093B
| Name of the Line |  | Main-I Protection |  | Avialibility |  | Date of testing | Main-II Protection |  | Avialibility |  | Date of testing | LBB Protection | Avialibility | Date of testing
|  |  | (Make & Model) |  | (In service or not) |  |  | (Make & Model) |  | (In service or not) |  |  | (Make & Model) | (In service or not)
2) | 220kV Subhasgram- Subhasgram Line-2 |  | AREVA, MICOM P 442 |  | YES |  | 2015 | Siemens, SIPROTEC- 7SA52 |  | Yes |  | 2015 | AREVA, MCTI | YES | 2011
| Name of the Line |  | PLCC/Protection Coupler |  | Avialibility |  | Date of testing | Disturbance recorder (DR) |  | Time Synchr.Unit |  | Date of testing | Any Other
|  |  | (Make & Model) |  | (In service or not) |  |  | (Make & Model) |  | (Make & Model) |  |  | Protection
2) | 220kV Subhasgram- Subhasgram Line-2 |  | Owned by WBSETCL |  | Yes |  |  | In built in Main I |  | Arbitor, 1093B
| Name of the Line |  | Main-I Protection |  | Avialibility |  | Date of testing | Main-II Protection |  | Avialibility |  | Date of testing | LBB Protection | Avialibility | Date of testing
|  |  | (Make & Model) |  | (In service or not) |  |  | (Make & Model) |  | (In service or not) |  |  | (Make & Model) | (In service or not)
3) | 220kV Subhasgram- KLC Bantala Line |  | AREVA, MICOM P 442 |  | YES |  | 2014 | Siemens, SIPROTEC- 7SA52 |  | Yes |  | 2014 | AREVA, MCTI | YES | 2011
| Name of the Line |  | PLCC/Protection Coupler |  | Avialibility |  | Date of testing | Disturbance recorder (DR) |  | Time Synchr.Unit |  | Date of testing | Any Other
|  |  | (Make & Model) |  | (In service or not) |  |  | (Make & Model) |  | (Make & Model) |  |  | Protection
3) | 220kV Subhasgram- KLC Bantala Line |  | Owned by WBSETCL |  | Yes |  |  | In built in Main I |  | Arbitor, 1093B
| Name of the Line |  | Main-I Protection |  | Avialibility |  | Date of testing | Main-II Protection |  | Avialibility |  | Date of testing | LBB Protection | Avialibility | Date of testing
|  |  | (Make & Model) |  | (In service or not) |  |  | (Make & Model) |  | (In service or not) |  |  | (Make & Model) | (In service or not)
4) | 220kV Subhasgram- Newtown Line |  | AREVA, MICOM P 442 |  | YES |  | 2014 | Siemens, SIPROTEC- 7SA52 |  | Yes |  | 2014 | AREVA, MCTI | YES | 2011
| Name of the Line |  | PLCC/Protection Coupler |  | Avialibility |  | Date of testing | Disturbance recorder (DR) |  | Time Synchr.Unit |  | Date of testing | Any Other
|  |  | (Make & Model) |  | (In service or not) |  |  | (Make & Model) |  | (Make & Model) |  |  | Protection
4) | 220kV Subhasgram- Newtown Line |  | Owned by WBSETCL |  | Yes |  |  | In built in Main I |  | Arbitor, 1093B
| Name of the Line |  | Main-I Protection |  | Avialibility |  | Date of testing | Main-II Protection |  | Avialibility |  | Date of testing | LBB Protection | Avialibility | Date of testing
|  |  | (Make & Model) |  | (In service or not) |  |  | (Make & Model) |  | (In service or not) |  |  | (Make & Model) | (In service or not)
5) | 220kV Subhasgram Future Line #1 |  | Siemens Siprotech 7SA522 |  | YES |  | 2015 | Micom P444 |  | Yes |  | 2015 | Siemens 7VK61 | YES | 2015
| Name of the Line |  | PLCC/Protection Coupler |  | Avialibility |  | Date of testing | Disturbance recorder (DR) |  | Time Synchr.Unit |  | Date of testing | Any Other
|  |  | (Make & Model) |  | (In service or not) |  |  | (Make & Model) |  | (Make & Model) |  |  | Protection
5) | 220kV Subhasgram Future Line #1 |  | NA |  |  |  |  | In built in Main I |  | Arbitor, 1093B |  | 2015
| Name of the Line |  | Main-I Protection |  | Avialibility |  | Date of testing | Main-II Protection |  | Avialibility |  | Date of testing | LBB Protection | Avialibility | Date of testing
|  |  | (Make & Model) |  | (In service or not) |  |  | (Make & Model) |  | (In service or not) |  |  | (Make & Model) | (In service or not)
6) | 220kV Subhasgram Future Line #2 |  | Siemens Siprotech 7SA522 |  | YES |  | 2015 | Micom P444 |  | Yes |  | 2015 | Siemens 7VK61 | YES | 2015
| Name of the Line |  | PLCC/Protection Coupler |  | Avialibility |  | Date of testing | Disturbance recorder (DR) |  | Time Synchr.Unit |  | Date of testing | Any Other
|  |  | (Make & Model) |  | (In service or not) |  |  | (Make & Model) |  | (Make & Model) |  |  | Protection
6) | 220kV Subhasgram Future Line #2 |  | NA |  |  |  |  | In built in Main I |  | Arbitor, 1093B |  | 2015
13) | Line Parameter
1) | Name of Line |  |  | 220 KV Subhasgram Subhasgram Line1 |  |  | 220 KV Subhasgram Subhasgram Line 2 | 220 KV Subhasgram KLC Bantala Line | 220 KV Subhasgram Newtown Line
2) | Line Length |  |  | 0.8 |  |  | 0.8 | 19 | 22.5
3) | Line Parameters
(In Ohms/Per KM/Per Phase Primary Value)
| RI |  |  | 0.06997 |  |  | 0.06997 | 0.084 | 0.084
| XI |  |  | 0.3971 |  |  | 0.3971 | 0.406 | 0.406
Rp
Xp
| RoM |  |  | 0 |  |  | 0
| XoM |  |  | 0.803 |  |  | 0.803
A) | Recent Relay setting
B) | Adopted Relay setting
C) | Recommecoded Relay setting
14) | Other details for: |  |  | DC Supply
Control Building
1) | DC supply
2) |  |  |  | 220 V DC-I | 220 V DC-II | 50 V DC-I |  | 50 V DC-II
3) | C&R Panel |  |  | 244 | 243.84 | -- |  | --
4) | Relay Panel |  |  | 244.1 | 243.9 | -- |  | --
5) | PLCC Panel |  |  | -- | -- | 49.58 |  | 49.42
15) | Circuit Breaker
|  |  | (Make and Model) |  | Status of Breaker | No. of trip/close |  | PIR (Available | Date of Last Timing |  | Remarkes (if any)
[5 empty] | Available or not | coil & healthiness |  | or Not) | Taken
1) | 204 |  | CGL, 220-SFM-40A |  | Available | TC-2/CC-1 -OK |  | Available | 2015
2) | 205 |  | CGL, 220-SFM-40A |  | Available | TC-2/CC-1 -OK |  | Available | 2015
3) | 206 |  | CGL, 220-SFM-40A |  | Available | TC-2/CC-1 -OK |  | Not Available | 2015
4) | 207 |  | CGL, 220-SFM-40A |  | Available | TC-2/CC-1 -OK |  | Not Available | 2015
5) | 208 |  | CGL, 220-SFM-40A |  | Available | TC-2/CC-1 -OK |  | Not Available | 2015
6) | 209 |  | CGL, 220-SFM-40A |  | Available | TC-2/CC-1 -OK |  | Not Available | 2015
7) | 210 |  | CGL, 220-SFM-40A |  | Available | TC-2/CC-1 -OK |  | Not Available | 2015
8) | 212 |  | CGL, 220-SFM-40A |  | Available | TC-2/CC-1 -OK |  | Not Available | 2015
9) | 215 |  | Siemens , 3A2PFI |  | Available | TC-2/CC-1 -OK |  | Not Available | 2015
10) | 216 |  | Siemens , 3A2PFI |  | Available | TC-2/CC-1 -OK |  | Not Available | 2015
11) | 201 |  | Siemens , 3A2PFI |  | Available | TC-2/CC-1 -OK |  | Not Available | 2015
16) | Availability of Auxiliary System
| Auxiliary Supply |  | Source of Supply |  | Reliability of Supply |  | Average tripping
per month
1) | Supply 1 (33kV) |  | From tertiary of ICT#1 |  | OK |  | NIL
2) | Supply 2 (11kV) |  | From WBSEB Kalikapur S/S |  | OK |  | 25-30 Nos Approx
17) | DG Set
Make |  |  |  | Greaves
Rating |  |  |  | 250kVA
Whether DG set on Auto or manual |  |  |  | Manual
18) | Availability of UFR relay
Make |  | N/A
Setting |  | N/A
19) | Availability of dt/dr relay
Make |  | N/A
Setting |  | N/A
20) | Special Protection Scheme (SPS)
Available (Yes/No) |  | N/A
Verification |  | N/A
21) | Status of Correcting action based on Tripping analysis
22) | Any Other Observation/Comments

## 400 KV
ERPC::KOLKATA
DETAILS OF PROTECTION AUDIT
A) | General Imformation :
1) | Name of Sub-station |  |  | 400/220kV Subhasgram Substation |  |  | 2) | Date of commissioning 2007 |  | 3) | Type of Bus Switching Scheme: |  | 1 and half | Whether SLD collected of Not: |  | 5) | Name of Audit Team
6) | Instrument transformer
A | Current transformer (CT)
1 | Location of CT |  |  | 401 Bay |  |  | (Please fill-up for each CT)
a | Date of Testing |  |  | 2007
b | CT ratio Test
|  |  | Phase Identification |  | Make/Model |  | Core I |  | Core II |  | Core III |  | Core IV |  | Core V |  | Core VI
1 | Ratio Adopted | [5 empty] | Bus Bar Prot-I |  | Bus Bar Prot-II |  | Metering |  | Main-II & LBB |  | Main I
[7 empty] | 2000/1 |  | 2000-1 |  | 2000/1 |  | 1000/1 |  | 1000/1
2 | Ratio measured |  | R |  | CGL |  | 2000 |  | 2004.29 |  | 1997.5 |  | 2004.29 |  | 1995
|  |  | Y |  | CGL |  | 2001.43 |  | 2000 |  | 2002.86 |  | 1995 |  | 2002
|  |  | B |  | CGL |  | 1997.5 |  | 1995 |  | 2002.86 |  | 1997.5 |  | 1995
3 | Error calculated |  | R |  | CGL |  | 0 |  | 0.002 |  | -0.001 |  | 0.002 |  | -0.003
|  |  | Y |  | CGL |  | 0.001 |  | 0 |  | 0.001 |  | -0.003 |  | 0.001
|  |  | B |  | CGL |  | -0.001 |  | -0.003 |  | 0.001 |  | -0.001 |  | -0.003
1 | Location of CT |  |  | 402 Bay |  |  | (Please fill-up for each CT)
a | Date of Testing |  |  | 2007
b | CT ratio Test
|  |  | Phase Identification |  | Make/Model |  | Core I |  | Core II |  | Core III |  | Core IV |  | Core V |  | Core VI
1 | Ratio Adopted | [5 empty] | Differential |  | Transformer Back Up O/c & LBB |  | Metering |  | Main II |  | Main I
[7 empty] | 1000/1 |  | 1000/1 |  | 2000/1 |  | 1000/1 |  | 1000/1
2 | Ratio measured |  | R |  | CGL |  | 1002.5 |  | 1002.5 |  | 1995 |  | 2002.86 |  | 2002.5
|  |  | Y |  | CGL |  | 1005 |  | 1000 |  | 2007.5 |  | 2002.86 |  | 2005
|  |  | B |  | CGL |  | 1002.5 |  | 1000 |  | 2001.42 |  | 2004.28 |  | 2001.42
3 | Error calculated |  | R |  | CGL |  | 0.0025 |  | 0.0025 |  | -0.0025 |  | 0.0014 |  | 0.0013
|  |  | Y |  | CGL |  | 0.005 |  | 0 |  | 0.0038 |  | 0.0014 |  | 0.0013
|  |  | B |  | CGL |  | 0.0025 |  | 0 |  | 0.0007 |  | 0.0021 |  | 0.0007
1 | Location of CT |  |  | 403 Bay |  |  | (Please fill-up for each CT)
a | Date of Testing |  |  | 2007
b | CT ratio Test
|  |  | Phase Identification |  | Make/Model |  | Core I |  | Core II |  | Core III |  | Core IV |  | Core V |  | Core VI
1 | Ratio Adopted | [5 empty] | Bus Bar Prot-I |  | Bus Bar Prot-II |  | SPARE |  | Transformer Back UP O/C & LBB |  | Differential
[7 empty] | 2000/1 |  | 2000-1 |  |  |  | 1000/1 |  | 1000/1
2 | Ratio measured |  | R |  | CGL |  | 2007.5 |  | 2004.29 |  |  |  | 1000 |  | 997.5
|  |  | Y |  | CGL |  | 2004.28 |  | 2000 |  |  |  | 1003.75 |  | 1000
|  |  | B |  | CGL |  | 1998.5 |  | 1995 |  |  |  | 1000 |  | 1001.25
3 | Error calculated |  | R |  | CGL |  | 0.004 |  | 0.002 |  |  |  | -0.001 |  | 0.002
|  |  | Y |  | CGL |  | 0.002 |  | 0 |  |  |  | 0.004 |  | 0
|  |  | B |  | CGL |  | -0.001 |  | -0.003 |  |  |  | 0 |  | 0.001
1 | Location of CT |  |  | 404 Bay |  |  | (Please fill-up for each CT)
a | Date of Testing |  |  | 2007
b | CT ratio Test
|  |  | Phase Identification |  | Make/Model |  | Core I |  | Core II |  | Core III |  | Core IV |  | Core V |  | Core VI
1 | Ratio Adopted | [5 empty] | Bus Bar Prot-I |  | Bus Bar Prot-II |  | Metering |  | Main-II & LBB |  | Main I
[7 empty] | 2000/1 |  | 2000-1 |  | 2000/1 |  | 1000/1 |  | 1000/1
2 | Ratio measured |  | R |  | CGL |  | 2001 |  | 2005 |  | 2003.8 |  | 1994.9 |  | 2003
|  |  | Y |  | CGL |  | 1999.7 |  | 2002.5 |  | 2004.5 |  | 2001.7 |  | 2001.7
|  |  | B |  | CGL |  | 1998.1 |  | 2001.1 |  | 2003.5 |  | 2004 |  | 1997
3 | Error calculated |  | R |  | CGL |  | 0.05 |  | 0.25 |  | 0.19 |  | -0.255 |  | 0.15
|  |  | Y |  | CGL |  | -0.015 |  | 0.125 |  | 0.225 |  | 0.085 |  | 0.085
|  |  | B |  | CGL |  | -0.1 |  | 0.05 |  | 0.18 |  | 0.2 |  | -0.15
1 | Location of CT |  |  | 405 Bay |  |  | (Please fill-up for each CT)
a | Date of Testing |  |  | 2007
b | CT ratio Test
|  |  | Phase Identification |  | Make/Model |  | Core I |  | Core II |  | Core III |  | Core IV |  | Core V |  | Core VI
1 | Ratio Adopted | [5 empty] | Differential |  | Transformer Back UP O/c & LBB |  | Metering |  | Main-II |  | Main I
[7 empty] | 1000/1 |  | 1000/1 |  | 2000/1 |  | 1000/1 |  | 1000/1
2 | Ratio measured |  | R |  | CGL |  | 1000.7 |  | 1000.4 |  | 2002.5 |  | 1995.5 |  | 2000.1
|  |  | Y |  | CGL |  | 1000 |  | 1000.2 |  | 2004.91 |  | 1995.9 |  | 1996.5
|  |  | B |  | CGL |  | 1000.3 |  | 1000.3 |  | 2001.22 |  | 2000.6 |  | 1998.1
3 | Error calculated |  | R |  | CGL |  | 0.07 |  | 0.04 |  | 0.125 |  | -0.225 |  | 0.005
|  |  | Y |  | CGL |  | 0 |  | 0.02 |  | 0.246 |  | -0.175 |  | -0.175
|  |  | B |  | CGL |  | 0.03 |  | 0.03 |  | 0.06 |  | 0.03 |  | -0.1
1 | Location of CT |  |  | 406 Bay |  |  | (Please fill-up for each CT)
a | Date of Testing |  |  | 2007
b | CT ratio Test
|  |  | Phase Identification |  | Make/Model |  | Core I |  | Core II |  | Core III |  | Core IV |  | Core V |  | Core VI
1 | Ratio Adopted | [5 empty] | Bus Bar Prot-I |  | Bus Bar Prot-II |  | SPARE |  | Transformer Back Up O/c & LBB |  | Diff Prot
[7 empty] | 2000/1 |  | 2000-1 |  |  |  | 1000/1 |  | 1000/1
2 | Ratio measured |  | R |  | CGL |  | 2000.4 |  | 2002.3 |  |  |  | 1000.4 |  | 1000.1
|  |  | Y |  | CGL |  | 2001.7 |  | 2001.8 |  |  |  | 1000.8 |  | 1000.9
|  |  | B |  | CGL |  | 1999 |  | 2000.6 |  |  |  | 1001.3 |  | 1000.9
3 | Error calculated |  | R |  | CGL |  | 0.02 |  | 0.115 |  |  |  | 0.04 |  | 0.01
|  |  | Y |  | CGL |  | 0.085 |  | 0.09 |  |  |  | 0.08 |  | 0.09
|  |  | B |  | CGL |  | -0.05 |  | 0.03 |  |  |  | 0.13 |  | 0.09
1 | Location of CT |  |  | 415 Bay |  |  | (Please fill-up for each CT)
a | Date of Testing |  |  | 2015
b | CT ratio Test
|  |  | Phase Identification |  | Make/Model |  | Core I |  | Core II |  | Core III |  | Core IV |  | Core V |  | Core VI
1 | Ratio Adopted | [5 empty] | Bus Bar Prot-I |  | Bus Bar Prot-II |  | SPARE |  | Transformer Back Up O/c & LBB |  | Diff Prot
[7 empty] | 2000/1 |  | 2000-1 |  |  |  | 1000/1 |  | 1000/1
2 | Ratio measured |  | R |  | Siemens |  | 1990.05 |  | 1990.05 |  |  |  | 998.75 |  | 997.51
|  |  | Y |  | Siemens |  | 2010.05 |  | 2010.05 |  |  |  | 1003.74 |  | 1003.76
|  |  | B |  | Siemens |  | 2015 |  | 2015.11 |  |  |  | 997.5 |  | 997.5
3 | Error calculated |  | R |  | Siemens |  | 0.004975 |  | 0.004975 |  |  |  | 0.00125 |  | 0.00249
|  |  | Y |  | Siemens |  | -0.005025 |  | -0.005025 |  |  |  | -0.00374 |  | -0.00376
|  |  | B |  | Siemens |  | -0.0075 |  | -0.007555 |  |  |  | 0.0025 |  | 0.0025
1 | Location of CVT |  |  | S'dighi-S'gram line CVT |  |  | (Please fill-up for each CVT)
a | Date of Testing |  |  | 2007
b | CT ratio Test
|  |  | Phase Identification |  | Make/Model |  | Core I |  | Core II |  | Core III
1 | Ratio Adopted | [5 empty] | PROTECTION |  | PROTECTION |  | METERING
[7 empty] | 3636.36 |  | 3636.36 |  | 3636.36
2 | Ratio measured |  | R |  | CGL |  | 3626.87 |  | 3573.53 |  | 3626.87
|  |  | Y |  | CGL |  | 3575.76 |  | 3575.76 |  | 3630.77
|  |  | B |  | CGL |  | 3588.24 |  | 3588.24 |  | 3641.79
3 | Error calculated |  | R |  | CGL |  | 0.26 |  | 1.73 |  | 0.26
|  |  | Y |  | CGL |  | 1.67 |  | 1.67 |  | 0.15
|  |  | B |  | CGL |  | 1.32 |  | 1.32 |  | -0.15
1 | Location of CVT |  |  | JRT-S'gram line CVT |  |  | (Please fill-up for each CVT)
a | Date of Testing |  |  | 2007
b | CT ratio Test
|  |  | Phase Identification |  | Make/Model |  | Core I |  | Core II |  | Core III
1 | Ratio Adopted | [5 empty] | PROTECTION |  | PROTECTION |  | METERING
[7 empty] | 3636.36 |  | 3636.36 |  | 3636.36
2 | Ratio measured |  | R |  | CGL |  | 3593.75 |  | 3593.75 |  | 3650.79
|  |  | Y |  | CGL |  | 3655.74 |  | 3655.74 |  | 3655.74
|  |  | B |  | CGL |  | 3645.16 |  | 3645.16 |  | 3645.16
3 | Error calculated |  | R |  | CGL |  | 1.17 |  | 1.17 |  | -0.4
|  |  | Y |  | CGL |  | -0.53 |  | -0.53 |  | -0.53
|  |  | B |  | CGL |  | -0.24 |  | -0.24 |  | -0.24
Availability of Protection System
8) | Bus Bar relay (upto 400KV)
1) | Make and Model of Bus Bar relay |  |  | Main I & Main II- AREVA FAC34
2) | Whethr stability Checks done or not |  |  |  | Yes
3) | Date of Testing |  |  |  | 2007
4) | Remarks (if any) |  |  |  | --
9) | Sub-station protection and monitorining Equipments
Sl. No. | System |  | LBB |  | Avialibility |  | Date of testing | Event Logger |  | Avialibility |  | Synchronising |  | Synchro Check | Setting of
|  |  | (Make & Model) |  | (In service or not) |  |  | (Make & Model) |  | (In service or not) |  | Facility Available or not |  | Relay (Make & Model) | Synchro Check Reley
1) | 400kV System |  | AREVA, MCTI 40 |  | Yes |  | 2011 | AREVA, C-264 |  | Yes |  | Yes |  | AREVA SKD 11 | ϕ= ± 35˚, V= 90%, t= 2 Sec
10) | Transmission Line Protection
SL. No. | Name of the Line |  | Main-I Protection |  | Avialibility |  | Date of testing | Main-II Protection |  | Avialibility |  | Date of testing | LBB Protection | Avialibility | Date of testing
|  |  | (Make & Model) |  | (In service or not) |  |  | (Make & Model) |  | (In service or not) |  |  | (Make & Model) | (In service or not)
1) | 400kV Subhasgram- Sagardighi Line |  | AREVA, MICOM-P 442 |  | YES |  | 2011 | Siemens, SIPROTEC- 7SA52 |  | Yes |  | 2011 | AREVA, MCTI | YES | 2011
| Name of the Line |  | PLCC/Protection Coupler |  | Avialibility |  | Date of testing | Disturbance recorder (DR) |  | Time Synchr.Unit |  | Date of testing | Any Other
|  |  | (Make & Model) |  | (In service or not) |  |  | (Make & Model) |  | (Make & Model) |  |  | Protection
1) | 400kV Subhasgram- Sagardighi Line |  | BPL, 9505 V3 |  | Yes |  | 2011 | In built in Main I |  | Arbitor, 1093B |  | 2011
| Name of the Line |  | Main-I Protection |  | Avialibility |  | Date of testing | Main-II Protection |  | Avialibility |  | Date of testing | LBB Protection | Avialibility | Date of testing
|  |  | (Make & Model) |  | (In service or not) |  |  | (Make & Model) |  | (In service or not) |  |  | (Make & Model) | (In service or not)
2) | 400kV Subhasgram-Jeerat Line |  | AREVA, MICOM P 442 |  | YES |  | 2011 | Siemens, SIPROTEC- 7SA52 |  | Yes |  | 2011 | AREVA, MCTI | YES | 2011
| Name of the Line |  | PLCC/Protection Coupler |  | Avialibility |  | Date of testing | Disturbance recorder (DR) |  | Time Synchr.Unit |  | Date of testing | Any Other
|  |  | (Make & Model) |  | (In service or not) |  |  | (Make & Model) |  | (Make & Model) |  |  | Protection
2) | 400kV Subhasgram-Jeerat Line |  | ABB- ETL 41 |  | Yes |  | 2011 | In built in Main I |  | Arbitor, 1093B |  | 2011
11) | Transformer Protection
| Name of ICT |  | Differential Protection |  | REP Protection |  | Back-up Over Current Protection (Make & Model) |  | Over Flux Protection |  | OTI/WTI Indication | Buchola/ PRO | Any Other | Any Other | Date of testing | LA Rating | LA Rating
|  |  | (Make & Model) |  | (Make & Model) |  |  |  | (Make & Model) |  | Working or not |  | Protection | Protection |  | HV Side | IV Side
1) | 315MVA ICT#1 |  | AREVA, MICOM P633 |  | AREVA, CAG14 |  | AREVA, CDD31 |  | AREVA, GTTM22 |  | Yes | Yes | -- | -- | 2011 | 390 kV | 216 kV
2) | 315MVA ICT#2 |  | AREVA, MICOM P633 |  | AREVA, CAG14 |  | AREVA, CDD31 |  | AREVA, GTTM22 |  | Yes | Yes | -- | -- | 2011 | 390 kV | 216 kV
3) | 500 MVA ICT |  | Siemens Siprotech 7UT613 |  |  |  | Siemens Siprotech 7SJ80 |  | Siemens Siprotech 7SR242 |  | Yes | Yes | - | - | 2015 | 336 KV | 216 KV
12) | Reactor Protection
| Name of Reactor |  | Differential Protection |  | REP Protection |  | Back-up Over Impedance Protection (Make & Model) |  | OTI/WTI Indication | Buchola/ PRO | Any Other | Date of testing | LA Rating
|  |  | (Make & Model) |  | (Make & Model) |  |  |  | Working or not |  | Protection |  | HV Side
1) | 50 MVAR Line Reacotor |  | ABB, RADHA |  | ABB, RADHD |  | ABB, RAKZB |  | Yes | Yes | -- | 2011 | 390 kV
13) | Line Parameter
1) | Name of Line |  |  | 400 kV Subhasgram-Sagardighi Line
2) | Line Length
3) | Line Parameters
(In Ohms/Per KM/Per Phase Primary Value)
| RI |  |  | 0.029792
| XI |  |  | 0.332
| Rp |  |  | 0.16192
| Xp |  |  | 1.24
| RoM |  |  | --
| XoM |  |  | --
A) | Recent Relay setting
B) | Adopted Relay setting
C) | Recommecoded Relay setting
13) | Line Parameter
1) | Name of Line |  |  | 400 kV Subhasgram-Jeerat Line
2) | Line Length
3) | Line Parameters
(In Ohms/Per KM/Per Phase Primary Value)
| RI |  |  | 0.029792
| XI |  |  | 0.332
| Rp |  |  | 0.16192
| Xp |  |  | 1.24
| RoM |  |  | --
| XoM |  |  | --
A) | Recent Relay setting
B) | Adopted Relay setting
C) | Recommecoded Relay setting
14) | Other details for: |  |  | DC Supply
Control Building
1) | DC supply
2) |  |  |  | 220 V DC-I | 220 V DC-II | 50 V DC-I |  | 50 V DC-II
3) | C&R Panel |  |  | 244 | 243.84 | -- |  | --
4) | Relay Panel |  |  | 244.1 | 243.9 | -- |  | --
5) | PLCC Panel |  |  | -- | -- | 49.58 |  | 49.42
15) | Circuit Breaker
|  |  | (Make and Model) |  | Status of Breaker | No. of trip/close |  | PIR (Available | Date of Last Timing |  | Remarkes (if any)
[5 empty] | Available or not | coil & healthiness |  | or Not) | Taken
1) | Sagardighi bay- 40152 |  | CGL, 400-SFM-40A |  | Available | TC-2/CC-1 -OK |  | Available | 2011
2) | Tie bay- 40252 |  | CGL, 400-SFM-40A |  | Available | TC-2/CC-1 -OK |  | Available | 2011
3) | ICT#1 bay- 40352 |  | CGL, 400-SFM-40A |  | Available | TC-2/CC-1 -OK |  | Not Available | 2011
4) | Jeerat bay- 40452 |  | CGL, 400-SFM-40A |  | Available | TC-2/CC-1 -OK |  | Not Available | 2011
5) | Tie bay- 40552 |  | CGL, 400-SFM-40A |  | Available | TC-2/CC-1 -OK |  | Not Available | 2011
6) | ICT#2 bay- 40652 |  | CGL, 400-SFM-40A |  | Available | TC-2/CC-1 -OK |  | Not Available | 2011
7) | ICT#5 Main bay 41552 |  | Siemens , 3A2PFI |  | Available | TC-2/CC-1 -OK |  | Not Available | 2015
16) | Availability of Auxiliary System
| Auxiliary Supply |  | Source of Supply |  | Reliability of Supply |  | Average tripping
per month
1) | Supply 1 (33kV) |  | From tertiary of ICT#1 |  | OK |  | NIL
2) | Supply 2 (11kV) |  | From WBSEB Kalikapur S/S |  | OK |  | 25-30 Nos Approx
17) | DG Set
Make |  |  |  | Greaves
Rating |  |  |  | 250kVA
Whether DG set on Auto or manual |  |  |  | Manual
18) | Availability of UFR relay
Make |  | N/A
Setting |  | N/A
19) | Availability of dt/dr relay
Make |  | N/A
Setting |  | N/A
20) | Special Protection Scheme (SPS)
Available (Yes/No) |  | N/A
Verification |  | N/A
21) | Status of Correcting action based on Tripping analysis
22) | Any Other Observation/Comments